## wind
Capital Cost baseline | OPEX baseline | Useful Life | Fixed OPEX inflation rate | Days of year | Hours of day | Power Density at Site | Wind Class applicable as IEC standards | Selected Turbine's rotor diameter | Swept Area | Tower Height | Power Density of Turbine | Avg Speed (based on location) | Turbine Rated power | Wind turbine Output multiplier 1 | Wind turbine Output multiplier 2 | Wind turbine Output multiplier 3 | Wind turbine space required for 2MW | Fail/ year | Down-time (hrs) | Degradation
360000000 | 9000000 | 20 | 0.1 | 365 | 24 | 428 |  | 122 | 11690 | 108 | 188.19 | 7.8 | 2.2 | 0.46 | 0.74 | 0.98 | 6100 | 1 | 72 | 1.5
Month | Per Month Energy Output | Output Prop
1 | 0.84 | 0.07
2 | 0.92 | 0.076667
3 | 0.93 | 0.0775
4 | 1.08 | 0.09
5 | 1.28 | 0.10667
6 | 1.2 | 0.1
7 | 1.18 | 0.098333
8 | 1.07 | 0.089167
9 | 1.02 | 0.085
10 | 0.82 | 0.068333
11 | 0.8 | 0.066667
12 | 0.86 | 0.071667
Month | Average Day Time (hours) | Windspeed at 100m
1 | 1 | 7.0064
1 | 2 | 7.2145
1 | 3 | 7.3533
1 | 4 | 7.2145
1 | 5 | 6.4514
1 | 6 | 5.5496
1 | 7 | 5.2028
1 | 8 | 4.9947
1 | 9 | 4.7866
1 | 10 | 4.6478
1 | 11 | 4.5091
1 | 12 | 4.5091
1 | 13 | 4.7172
1 | 14 | 5.3415
1 | 15 | 5.619
1 | 16 | 5.619
1 | 17 | 5.4803
1 | 18 | 5.5496
1 | 19 | 5.619
1 | 20 | 5.8271
1 | 21 | 6.174
1 | 22 | 6.5208
1 | 23 | 6.7289
1 | 24 | 6.8677
2 | 1 | 7.0163
2 | 2 | 7.1352
2 | 3 | 6.9569
2 | 4 | 6.5406
2 | 5 | 5.4704
2 | 6 | 4.6974
2 | 7 | 4.3406
2 | 8 | 4.1622
2 | 9 | 4.0433
2 | 10 | 4.0433
2 | 11 | 4.0433
2 | 12 | 4.0433
2 | 13 | 4.1622
2 | 14 | 4.6974
2 | 15 | 5.0541
2 | 16 | 5.1731
2 | 17 | 5.2325
2 | 18 | 5.5298
2 | 19 | 5.8271
2 | 20 | 6.065
2 | 21 | 6.3623
2 | 22 | 6.6001
2 | 23 | 6.7785
2 | 24 | 6.7785
3 | 1 | 6.7913
3 | 2 | 6.6711
3 | 3 | 6.4908
3 | 4 | 6.1302
3 | 5 | 5.2888
3 | 6 | 4.6277
3 | 7 | 4.207
3 | 8 | 3.9666
3 | 9 | 3.7863
3 | 10 | 3.7863
3 | 11 | 3.8464
3 | 12 | 3.9666
3 | 13 | 4.207
3 | 14 | 4.6277
3 | 15 | 5.2888
3 | 16 | 5.7696
3 | 17 | 6.1903
3 | 18 | 6.2504
3 | 19 | 6.4307
3 | 20 | 6.611
3 | 21 | 6.8514
3 | 22 | 7.1519
3 | 23 | 7.3923
3 | 24 | 7.3923
4 | 1 | 12.4206
4 | 2 | 11.8921
4 | 3 | 11.0112
4 | 4 | 9.3375
4 | 5 | 7.5757
4 | 6 | 6.6067
4 | 7 | 6.3424
4 | 8 | 6.3424
4 | 9 | 6.4305
4 | 10 | 6.6067
4 | 11 | 6.871
4 | 12 | 7.2233
4 | 13 | 7.6638
4 | 14 | 8.2804
4 | 15 | 9.1613
4 | 16 | 9.866
4 | 17 | 10.5707
4 | 18 | 11.3635
4 | 19 | 11.8921
4 | 20 | 12.2444
4 | 21 | 12.4206
4 | 22 | 12.5087
4 | 23 | 12.4206
4 | 24 | 12.1563
5 | 1 | 11.8735
5 | 2 | 11.7063
5 | 3 | 11.0373
5 | 4 | 9.9503
5 | 5 | 9.2814
5 | 6 | 8.9469
5 | 7 | 8.7797
5 | 8 | 8.7797
5 | 9 | 8.8633
5 | 10 | 9.1142
5 | 11 | 9.4486
5 | 12 | 9.6995
5 | 13 | 9.7831
5 | 14 | 10.0339
5 | 15 | 10.5356
5 | 16 | 11.1209
5 | 17 | 11.7063
5 | 18 | 12.1243
5 | 19 | 12.2916
5 | 20 | 12.4588
5 | 21 | 12.5424
5 | 22 | 12.3752
5 | 23 | 12.2916
5 | 24 | 12.3752
6 | 1 | 14.7501
6 | 2 | 14.5083
6 | 3 | 14.0247
6 | 4 | 13.4202
6 | 5 | 12.9366
6 | 6 | 12.453
6 | 7 | 12.453
6 | 8 | 12.5739
6 | 9 | 12.9366
6 | 10 | 13.2993
6 | 11 | 13.662
6 | 12 | 14.0247
6 | 13 | 14.1456
6 | 14 | 14.7501
6 | 15 | 15.1128
6 | 16 | 15.2337
6 | 17 | 15.4755
6 | 18 | 15.7174
6 | 19 | 15.8383
6 | 20 | 15.8383
6 | 21 | 15.9592
6 | 22 | 16.0801
6 | 23 | 16.0801
6 | 24 | 15.9592
7 | 1 | 14.7542
7 | 2 | 14.6333
7 | 3 | 14.3914
7 | 4 | 13.9077
7 | 5 | 13.303
7 | 6 | 12.8192
7 | 7 | 12.5774
7 | 8 | 12.5774
7 | 9 | 12.9402
7 | 10 | 13.303
7 | 11 | 13.7867
7 | 12 | 14.2705
7 | 13 | 14.7542
7 | 14 | 15.117
7 | 15 | 15.238
7 | 16 | 14.9961
7 | 17 | 14.8752
7 | 18 | 14.7542
7 | 19 | 14.8752
7 | 20 | 14.9961
7 | 21 | 15.238
7 | 22 | 15.238
7 | 23 | 15.3589
7 | 24 | 15.238
8 | 1 | 15.9943
8 | 2 | 15.8576
8 | 3 | 15.3108
8 | 4 | 14.6272
8 | 5 | 13.6703
8 | 6 | 12.9868
8 | 7 | 12.5767
8 | 8 | 12.5767
8 | 9 | 12.9868
8 | 10 | 13.2602
8 | 11 | 13.5336
8 | 12 | 14.2171
8 | 13 | 14.6272
8 | 14 | 15.0374
8 | 15 | 15.1741
8 | 16 | 15.1741
8 | 17 | 15.1741
8 | 18 | 15.3108
8 | 19 | 15.4475
8 | 20 | 15.5842
8 | 21 | 15.8576
8 | 22 | 15.9943
8 | 23 | 15.8576
8 | 24 | 15.5842
9 | 1 | 10.4137
9 | 2 | 10.2342
9 | 3 | 9.9649
9 | 4 | 9.0671
9 | 5 | 8.1694
9 | 6 | 7.6307
9 | 7 | 7.3614
9 | 8 | 7.2717
9 | 9 | 7.2717
9 | 10 | 7.541
9 | 11 | 7.8103
9 | 12 | 8.1694
9 | 13 | 8.6183
9 | 14 | 8.9773
9 | 15 | 9.2467
9 | 16 | 9.3364
9 | 17 | 9.6955
9 | 18 | 9.9649
9 | 19 | 10.0546
9 | 20 | 10.2342
9 | 21 | 10.4137
9 | 22 | 10.5035
9 | 23 | 10.5035
9 | 24 | 10.5035
10 | 1 | 7.6863
10 | 2 | 7.4688
10 | 3 | 7.1062
10 | 4 | 6.5986
10 | 5 | 5.5835
10 | 6 | 4.5683
10 | 7 | 4.0607
10 | 8 | 3.9157
10 | 9 | 3.9882
10 | 10 | 3.9882
10 | 11 | 4.1332
10 | 12 | 4.2782
10 | 13 | 4.5683
10 | 14 | 5.3659
10 | 15 | 5.801
10 | 16 | 6.0911
10 | 17 | 6.1636
10 | 18 | 6.4536
10 | 19 | 6.8162
10 | 20 | 7.2513
10 | 21 | 7.6138
10 | 22 | 7.8314
10 | 23 | 7.9039
10 | 24 | 7.8314
11 | 1 | 6.9331
11 | 2 | 6.9985
11 | 3 | 6.9985
11 | 4 | 6.8023
11 | 5 | 6.2136
11 | 6 | 5.1017
11 | 7 | 4.4476
11 | 8 | 4.0552
11 | 9 | 3.859
11 | 10 | 3.7936
11 | 11 | 3.7936
11 | 12 | 3.7936
11 | 13 | 3.9898
11 | 14 | 4.5784
11 | 15 | 4.7747
11 | 16 | 4.8401
11 | 17 | 4.8401
11 | 18 | 4.8401
11 | 19 | 4.9709
11 | 20 | 5.2979
11 | 21 | 5.6904
11 | 22 | 6.0828
11 | 23 | 6.4752
11 | 24 | 6.7369
12 | 1 | 7.5487
12 | 2 | 7.6953
12 | 3 | 7.6953
12 | 4 | 7.5487
12 | 5 | 7.0357
12 | 6 | 5.9364
12 | 7 | 5.4233
12 | 8 | 5.0569
12 | 9 | 4.837
12 | 10 | 4.7637
12 | 11 | 4.6905
12 | 12 | 4.7637
12 | 13 | 5.0569
12 | 14 | 5.6432
12 | 15 | 5.9364
12 | 16 | 6.0096
12 | 17 | 6.0829
12 | 18 | 6.1562
12 | 19 | 6.3761
12 | 20 | 6.6692
12 | 21 | 6.9624
12 | 22 | 7.2555
12 | 23 | 7.4754
12 | 24 | 7.7686

## solar
Capital Cost Baseline | OPEX Baseline | Useful Life | Fixed OPEX Inflation Rate | Specific Yield | 1 MW Space Required | Total Energy | Fail/ year | Down-time (hrs) | Degradation per year | Existing/ Year 0 Total Cost
171000000 | 175000 | 15 | 0.1 | - | 12000 | 1769.5 | 2 | 24 | 0.8 | 80000000
Months | Monthly Energy Output | Output proportion of year | average sun available hours | average sun unavailable hours |  |  | BESS (Backup to solar and critical loads)
1 | 151.65 | 0.085702 | 341 | 403
2 | 148 | 0.083639 | 308 | 364 |  |  | Capital Cost baseline | 112500000 | PKR per MWh
3 | 169.45 | 0.095762 | 403 | 341 |  |  | OPEX baseline fixed | 400000 | PKR per MWh per month | Now Valid Value is Rec.
4 | 160.95 | 0.090958 | 390 | 330 |  |  | Useful Life | 10
5 | 157.9 | 0.089234 | 403 | 341 |  |  | Depreciation rate | 5 | %
6 | 136.65 | 0.077225 | 390 | 330 |  |  | Fixed OPEX inflation rate | 0.1
7 | 121.35 | 0.068579 | 403 | 341
8 | 128.85 | 0.072817 | 390 | 330
9 | 147.35 | 0.083272 | 403 | 341
10 | 160.7 | 0.090817 | 330 | 390
11 | 144.45 | 0.081633 | 300 | 420
12 | 143.7 | 0.081209 | 330 | 403
Month | Average Day Time (hours) | KW PV Output per MW
1 | 1 | 0
1 | 2 | 0
1 | 3 | 0
1 | 4 | 0
1 | 5 | 0
1 | 6 | 0
1 | 7 | 0
1 | 8 | 22
1 | 9 | 240
1 | 10 | 443
1 | 11 | 596
1 | 12 | 695
1 | 13 | 732
1 | 14 | 704
1 | 15 | 617
1 | 16 | 471
1 | 17 | 284
1 | 18 | 40
1 | 19 | 0
1 | 20 | 0
1 | 21 | 0
1 | 22 | 0
1 | 23 | 0
1 | 24 | 0
2 | 1 | 0
2 | 2 | 0
2 | 3 | 0
2 | 4 | 0
2 | 5 | 0
2 | 6 | 0
2 | 7 | 0
2 | 8 | 36
2 | 9 | 262
2 | 10 | 465
2 | 11 | 624
2 | 12 | 731
2 | 13 | 773
2 | 14 | 753
2 | 15 | 670
2 | 16 | 532
2 | 17 | 347
2 | 18 | 91
2 | 19 | 0
2 | 20 | 0
2 | 21 | 0
2 | 22 | 0
2 | 23 | 0
2 | 24 | 0
3 | 1 | 0
3 | 2 | 0
3 | 3 | 0
3 | 4 | 0
3 | 5 | 0
3 | 6 | 0
3 | 7 | 1
3 | 8 | 83
3 | 9 | 301
3 | 10 | 496
3 | 11 | 642
3 | 12 | 743
3 | 13 | 781
3 | 14 | 763
3 | 15 | 661
3 | 16 | 524
3 | 17 | 343
3 | 18 | 129
3 | 19 | 1
3 | 20 | 0
3 | 21 | 0
3 | 22 | 0
3 | 23 | 0
3 | 24 | 0
4 | 1 | 0
4 | 2 | 0
4 | 3 | 0
4 | 4 | 0
4 | 5 | 0
4 | 6 | 0
4 | 7 | 15
4 | 8 | 145
4 | 9 | 334
4 | 10 | 508
4 | 11 | 639
4 | 12 | 719
4 | 13 | 744
4 | 14 | 707
4 | 15 | 618
4 | 16 | 480
4 | 17 | 314
4 | 18 | 132
4 | 19 | 10
4 | 20 | 0
4 | 21 | 0
4 | 22 | 0
4 | 23 | 0
4 | 24 | 0
5 | 1 | 0
5 | 2 | 0
5 | 3 | 0
5 | 4 | 0
5 | 5 | 0
5 | 6 | 0
5 | 7 | 36
5 | 8 | 160
5 | 9 | 326
5 | 10 | 482
5 | 11 | 600
5 | 12 | 673
5 | 13 | 693
5 | 14 | 658
5 | 15 | 574
5 | 16 | 447
5 | 17 | 290
5 | 18 | 134
5 | 19 | 19
5 | 20 | 0
5 | 21 | 0
5 | 22 | 0
5 | 23 | 0
5 | 24 | 0
6 | 1 | 0
6 | 2 | 0
6 | 3 | 0
6 | 4 | 0
6 | 5 | 0
6 | 6 | 0
6 | 7 | 35
6 | 8 | 132
6 | 9 | 271
6 | 10 | 414
6 | 11 | 527
6 | 12 | 595
6 | 13 | 623
6 | 14 | 594
6 | 15 | 518
6 | 16 | 410
6 | 17 | 274
6 | 18 | 135
6 | 19 | 28
6 | 20 | 0
6 | 21 | 0
6 | 22 | 0
6 | 23 | 0
6 | 24 | 0
7 | 1 | 0
7 | 2 | 0
7 | 3 | 0
7 | 4 | 0
7 | 5 | 0
7 | 6 | 0
7 | 7 | 19
7 | 8 | 98
7 | 9 | 213
7 | 10 | 337
7 | 11 | 441
7 | 12 | 515
7 | 13 | 542
7 | 14 | 525
7 | 15 | 465
7 | 16 | 362
7 | 17 | 243
7 | 18 | 124
7 | 19 | 29
7 | 20 | 0
7 | 21 | 0
7 | 22 | 0
7 | 23 | 0
7 | 24 | 0
8 | 1 | 0
8 | 2 | 0
8 | 3 | 0
8 | 4 | 0
8 | 5 | 0
8 | 6 | 0
8 | 7 | 11
8 | 8 | 101
8 | 9 | 232
8 | 10 | 367
8 | 11 | 480
8 | 12 | 557
8 | 13 | 589
8 | 14 | 561
8 | 15 | 495
8 | 16 | 383
8 | 17 | 250
8 | 18 | 115
8 | 19 | 14
8 | 20 | 0
8 | 21 | 0
8 | 22 | 0
8 | 23 | 0
8 | 24 | 0
9 | 1 | 0
9 | 2 | 0
9 | 3 | 0
9 | 4 | 0
9 | 5 | 0
9 | 6 | 0
9 | 7 | 9
9 | 8 | 130
9 | 9 | 310
9 | 10 | 475
9 | 11 | 600
9 | 12 | 678
9 | 13 | 701
9 | 14 | 661
9 | 15 | 563
9 | 16 | 432
9 | 17 | 264
9 | 18 | 86
9 | 19 | 1
9 | 20 | 0
9 | 21 | 0
9 | 22 | 0
9 | 23 | 0
9 | 24 | 0
10 | 1 | 0
10 | 2 | 0
10 | 3 | 0
10 | 4 | 0
10 | 5 | 0
10 | 6 | 0
10 | 7 | 0
10 | 8 | 137
10 | 9 | 366
10 | 10 | 542
10 | 11 | 669
10 | 12 | 742
10 | 13 | 754
10 | 14 | 695
10 | 15 | 583
10 | 16 | 427
10 | 17 | 239
10 | 18 | 31
10 | 19 | 0
10 | 20 | 0
10 | 21 | 0
10 | 22 | 0
10 | 23 | 0
10 | 24 | 0
11 | 1 | 0
11 | 2 | 0
11 | 3 | 0
11 | 4 | 0
11 | 5 | 0
11 | 6 | 0
11 | 7 | 0
11 | 8 | 81
11 | 9 | 329
11 | 10 | 515
11 | 11 | 644
11 | 12 | 715
11 | 13 | 722
11 | 14 | 672
11 | 15 | 560
11 | 16 | 402
11 | 17 | 175
11 | 18 | 0
11 | 19 | 0
11 | 20 | 0
11 | 21 | 0
11 | 22 | 0
11 | 23 | 0
11 | 24 | 0
12 | 1 | 0
12 | 2 | 0
12 | 3 | 0
12 | 4 | 0
12 | 5 | 0
12 | 6 | 0
12 | 7 | 0
12 | 8 | 33
12 | 9 | 273
12 | 10 | 467
12 | 11 | 606
12 | 12 | 691
12 | 13 | 714
12 | 14 | 671
12 | 15 | 568
12 | 16 | 419
12 | 17 | 193
12 | 18 | 2
12 | 19 | 0
12 | 20 | 0
12 | 21 | 0
12 | 22 | 0
12 | 23 | 0
12 | 24 | 0

## grid
Capital Cost Baseline | Existing/ Year 0 Total Cost | Tariff baseline fixed | Tariff baseline variable- offpeak | Tariff baseline variable- peak | Fail/ year | Down-time (hrs) | Inflation Rate | Time to take load_primary | CO2 emissions
2000000 | 5762000 | 460000 | 45790 | 51590 | 40 | 3.67 | 0.1 | 0.25 | 350
per MW | PKR | tot | Rs. Per MWh | Rs. Per MWh | No. of Failures/Year | hours/failure | % | hr | kg/MWh | https://www.irena.org/-/media/Files/IRENA/Agency/Statistics/Statistical_Profiles/Asia/Pakistan_Asia_RE_SP.pdf
https://kpac.sharepoint.com/:b:/s/EngineeringTeam/ETPDVrU8w6ZArTNMSrZAWOEBi5TlzW6CBpoc_OhZnRMlQg?e=9SsQqa

## thermal_sources
Trifuel enginer generator (HFO+RLNG) |  |  | Gas Generator |  |  | HFO Generator |  |  | Diesel Generator
Operating baseline | 42700 | KJ/Kg | Operating baseline | 42700 | KJ/Kg | Operating baseline | 41100 | KJ/Kg | Operating baseline | 4.714 | kWh/litre
Capital Cost baseline | 153000000 | Rs./MW | Capital Cost baseline | 72000000 | Rs./MW | Capital Cost baseline | 136000000 | Rs./MW | Capital Cost baseline | 45000000 | Rs./MW
OPEX baseline fixed | 300000 | Rs.MW/month | OPEX baseline fixed | 300000 | Rs.MW/month | OPEX baseline fixed | 300000 | Rs.MW/month | OPEX baseline fixed | 150000 | Rs. Per month
OPEX baseline var | 4500 | Rs./MWh | OPEX baseline var | 3500 | Rs./MWh | OPEX baseline var | 4000 | Rs./MWh | OPEX baseline var | 1500 | Rs. Per MWh
Useful Life | 12 | years | Useful Life | 12 | years | Useful Life | 12 | years | Useful Life | 10 | years
Current Running Hours | 0 | hrs | Current Running Hours | 0 | hrs | Current Running Hours | 0 | hrs | Current Running Hours | - | hrs
OPEX inflation rate | 0.1 |  | Fixed OPEX inflation rate | 0.1 |  | Fixed OPEX inflation rate | 0.1 |  | Fixed OPEX inflation rate | 0.1
Depreciation rate | 8 | % | Depreciation rate | 8 | % | Depreciation rate | 8 | % | Depreciation rate | 8 | %
Cooling Load Feeding Capability | 220 | TR per MW | Cooling Load Feeding Capability | 243 | TR per MW | Cooling Load Feeding Capability | 220 | TR per MW | Cooling Load Feeding Capability | 115.5 | TR per MW
Min Loading | 30 | % | Min Loading | 30 | % | Min Loading | 30 | % | Min Loading | 30 | %
Max Loading | 98.5 | % | Max Loading | 98.5 | % | Max Loading | 98.5 | % | Max Loading | 98.5 | %
Failures per year | 3 |  | Failures per year | 8 |  | Failures per year | 5 |  | Failures per year | 0
Downtime per failure | 45 |  | Downtime per failure | 45 |  | Downtime per failure | 45 |  | Downtime per failure | 8
Time to take load_primary | 0.5 | hours | Time to take load_primary | 0.25 | hours | Time to take load_primary | 0.5 | hours | Time to take load_primary | 0.0083333 | hours
Time to take load_backup | 0.25 | hours | Time to take load_backup | 0.125 | hours | Time to take load_backup | 0.25 | hours | CO2 Emissions on Diesel | 800 | kg/MWh
CO2 Emissions on RLNG | 180 | kg/MWh | CO2 Emissions on RLNG | 180 | kg/MWh | CO2 Emissions on HFO | 270 | kg/MWh | Annual Degradation | 1 | %
CO2 Emissions on HFO | 270 | kg/MWh | Annual Degradation | 1.5 | % | Annual Degradation | 1.5 | %
Gas-based operation proportion | 60 | % | Existing/ Year 0 Cost | 25000000 | PKR
Annual Degradation | 1.5 | %
https://kpac.sharepoint.com/:b:/s/EngineeringTeam/ESKDzKHwlX9ElWJSu5ADlzQBrFF-At2BOZKNgqoxRgazqg?e=flJ3dM

## site_load
Load Profile
|  |  |  | Maximum Demand Load Day | Maximum Demand Load Night | Running Load Proportion | Cooling requirement in TR | Cooling electrical load | Critical Load proportion
Site Details |  |  | Year 1 | 5 | 5 | 70 | 900 | 0.7 | 20
COP of Electric chiller | 4.5 |  | Year 2 | 5 | 5 | 70 | 900 | 0.7 | 20
cooling hours per day | 16 | hrs | Year 3 | 5 | 5 | 70 | 900 | 0.7 | 20
Critical Production load Prop | 20 | % | Year 4 | 5 | 5 | 70 | 900 | 0.7 | 20
Summer Day cooling Demand Prop | 100 | % | Year 5 | 7 | 7 | 70 | 900 | 0.7 | 20
Summer Night cooling demand Prop | 85 | % | Year 6 | 7 | 7 | 70 | 900 | 0.7 | 20
Winter Day cooling demand Prop | 85 | % | Year 7 | 7 | 7 | 70 | 900 | 0.7 | 20
Winter Night cooling demand Prop | 0 | % | Year 8 | 7 | 7 | 70 | 900 | 0.7 | 20
land area for renewables | 24281 | sqm | Year 9 | 7 | 7 | 70 | 900 | 0.7 | 20
rooftop area for solar | 24000 | sqm | Year 10 | 7 | 7 | 70 | 900 | 0.7 | 20
capital inflation rate | 0.1 | % |  | MW | MW | % | TR | MW | %
Immediate Loss from Power Failure | 4640000 | PKR
Loss as Power remains suspended | 250000 | PKR/hr
Energy Profile
|  |  | Month | Grid Peak to Non Peak Energy | Unit monthly energy consumption (MWh / MW) | Length of day (hrs) | Length of night (hrs) | Season | Days | Existing Factory
Existing Factory |  |  | 1 | 0.257 | 278.3333 | 11 | 13 | Winter | 31 | 1169
Existing Factory Maximum Demand | 4.2 | MW | 2 | 0.231 | 282.1429 | 12 | 12 | Winter | 28 | 1185
|  |  | 3 | 0.211 | 251.9048 | 13 | 11 | Summer | 31 | 1058
|  |  | 4 | 0.208 | 278.8095 | 13 | 11 | Summer | 30 | 1171
|  |  | 5 | 0.201 | 252.1429 | 13 | 11 | Summer | 31 | 1059
|  |  | 6 | 0.226 | 256.4286 | 13 | 11 | Summer | 30 | 1077
|  |  | 7 | 0.22 | 261.9048 | 13 | 11 | Summer | 31 | 1100
|  |  | 8 | 0.222 | 251.6667 | 13 | 11 | Summer | 31 | 1057
|  |  | 9 | 0.237 | 270.4762 | 12 | 12 | Summer | 30 | 1136
|  |  | 10 | 0.228 | 273.3333 | 11 | 13 | Summer | 31 | 1148
|  |  | 11 | 0.247 | 255.9524 | 10 | 14 | Winter | 30 | 1075
|  |  | 12 | 0.245 | 285.7143 | 10 | 14 | Winter | 31 | 1200

## tariff
Fuel Tariffs | Value | Units
Natural Gas Tariff | 1200 | Rs./MMBTU | https://kpac.sharepoint.com/:b:/s/EngineeringTeam/EdP1OZ3CRKZJubBvcHCAiWgBpmWAU_dM2y9wVOEANXLujA?e=MycqHO
Natural Gas Transport Cost | 147.6 | Rs./MMBTU
Natural Gas Tariff (equivalent) | 29900 | Rs./MWh | 24.9167
Fuel inflation rate for Natural Gas | 0.05
CO2 Emissions for NG | 220 | kg/MWh
LNG Tariff | 4433.24 | Rs./MMBTU | https://kpac.sharepoint.com/:b:/s/EngineeringTeam/ETCgFiJr4ANHvb2Df7FgwnkB2lO9xbrz39jtiVpDZsaeew?e=JToVCw
LNG Transport Cost | 438.1649 | Rs./MMBTU
LNG Tariff (equivalent) | 110461.5633 | Rs./MWh
Fuel inflation rate for LNG | 0.05
CO2 Emissions for LNG | 220 | kg/MWh
LPG Tariff | 240000 | Rs./MT | https://kpac.sharepoint.com/:b:/s/EngineeringTeam/EWkB9jV6hJRMgixUjZMQXWIB4f8IffPyTr9euZH63SS58A?e=uxkcCp
LPG Transport Cost | 8000 | Rs./MT
LPG Tariff (equivalent) | 61479 | Rs./MWh
Fuel inflation rate for LPG | 0.05
CO2 Emissions for LPG | 250 | kg/MWh
Biogas Tariff | 1543 | Rs./MMBTU | NO Relevent Data Found
Biogas Transport Cost | 190 | Rs./MMBTU
Biogas Tariff (equivalent) | 61479 | Rs./MWh
Fuel inflation rate for Biogas | 0.05
CO2 Emissions for Biogas | 0 | kg/MWh
HFO Tariff | 194000 | Rs./MT | https://kpac.sharepoint.com/:b:/s/EngineeringTeam/EW2yXeriKOFMm30L_ucRtTwBWNpz3LTZkMVg0CyEodopyQ?e=BqGQSC
HFO Transport Cost | 6402 | Rs./T
HFO Tariff (equivalent) | 40000 | Rs./MWh
Fuel inflation rate for HFO | 0.05
CO2 Emissions for HFO | 500 | kg/MWh
Diesel Fuel Cost | 312.4 | Rs/Litre | https://kpac.sharepoint.com/:b:/s/EngineeringTeam/EfDmEZRuYv9GjgvbqpRF_KEB7T7z_54sBqdkNEe9AefLTg?e=sJrc2C
Diesel Transport Cost | 7 | Rs/Litre
Diesel Cost Equivalent | 72000 | Rs/MWh
Fuel inflation rate for Diesel | 0.05
CO2 Emissions for Diesel | 500 | kg/MWh

## Sheet1
Row data and its references
1. Capex and Opex for a grid-tied solar plant in the size range of 01 to 02MW. CAPEX for a high quality solar PV installation ranges from 0.55 to 0.57 cents per watt. Open you can assume at 7000 USD per MW per year.
1. Capex and Opex for BESS [2.0 PCS and 1.25 MWh storage]. BESS is primarily CAPEX not much OPEX. CAPEX depends on chemistry of storage, inverter selection and capability and discharge rate. The most common chemistry is LiPO4 , which has a CAPEX (with Power Conversion and System and Battery Management System) of $ 375 USD/Kwh.
1. What useful life of BESS is normally considered in feasibility studies? This significantly depends on usage (i.e. cycling) , more the Depth of Discharge, more the cycling lesser is the life. For LiPO4 with 2 to 3 cycles per day at 80% DoD and at 1 C (Discharge rate) you can get 6 to 7 years.
1. Capex and Opex for a 2.5MW wind turbine? You can assume a 1.2 million USD per MW for CAPEX and 30,000 USD per MW per year for OPEX.
| Cent | Cent to USD | 1 USD to PKR | PKR/W | PKR/MW |  |  | USD/MW | PKR/MW
Solar | 57 | 0.57 | 300 | 171 | 171000000 | CAPEX |  | 7000 | 2100000 | OPEX
|  | USD/kWh | 1 USD to PKR | PKR/kWh | PKR/MWh
BESS |  | 375 | 300 | 112500 | 112500000 | 7 ys | Useful Life
|  | USD/MW | 1 USD to PKR | PKR/MW |  |  |  | USD/MW | PKR/MW
Wind |  | 1200000 | 300 | 360000000 | CAPEX |  |  | 30000 | 9000000 | OPEX
In comparison to HFO, LNG shipping fuel can reduce NOX emissions by 85–95%, CO2 by 20%, and SOX by 100%
GW
7
CO2 Emissions on RLNG |  |  | 180 | kg/MWh | 216 | 180
NOX Emissions on RLNG |  |  |  | kg/MWh
CO2 Emissions on HFO |  |  | 270 | kg/MWh | 270 | 216
NOX Emissions on HFO |  |  |  | kg/MWh
A global fleet of 7.0 GW generating capacity reliant on domestic NG could emit 12 Tg CO2, 2.2–8.6 Tg CH4, 4.3 Gg NOx, and 2.6 Gg PM. Additional NOx and SO2 emissions would result from imported LNG, as LNG tankers burn dirty fuel oil