## Sheet1
MWh | M PKR |  |  | Grid MWh | PKR M
18169.9219 | 297.8301 | 342.6766 | 1530.2595 |  | 123.8482
18202.7999 | 487.5792 | 376.8352 | 1685.2014 |  | 146.95
16392.5944 | 314.6638 | 9.4458 | 38.5542 |  | 36.0604
16441.1458 | 335.049 | 18.9534 | 77.0466 |  | 42.9651
22887.3162 | 457.6003 | 26.5348 | 107.8652 |  | 50.1643
22935.8676 | 490.6387 | 0 | 0 |  | 44.0056
22984.419 | 524.1085 | 0 | 0 |  | 48.4061
23032.9704 | 562.796 | 13.2241 | 53.9759 |  | 60.0072

## scenario
Year | Solar Total Capacity MW | Solar Source Priority | BESS Total Capacity MW | BESS Source Priority | PPA Total Capacity MW | PPA Source Priority | Gas Generator Total Capacity MW | Gas Generator Source Priority | Grid Total Capacity MW | Grid Source Priority | Diesel Generator Total Capacity MW | Diesel Generator Source Priority
0 | 2 | 0 | 0 | 0 | 0 | 1 | 1.5 | 1 | 4.5 | 2 | 0 | 4
1 | 0 | 0 | 1.5 | 0 | 2 | 1 | 0 | 1 | 0 | 2 | 1 | 4
2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 4
3 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 2 | 0 | 4
4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 4
5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 4
6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 4
7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 4
8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 | 0 | 4

## power
year | month | hour | Prod Demand in MW | Cooling demand in TR | Free Cooling available in TR | BESS Charging Demand | Total power demand incl. Cooling & BESS in MW | Solar Output in MW | Solar Loading in % | BESS Output in MW | BESS Loading in % | PPA Output in MW | PPA Loading in % | Gas Generator Output in MW | Gas Generator Loading in % | Grid Output in MW | Grid Loading in % | Diesel Generator Output in MW | Diesel Generator Loading in % | Final Unserved Load
1 | 1 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 1 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 1 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 1 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 1 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 1 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 1 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 1 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.043648 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.76403 | 16.9783 | 0 | 0 | 0
1 | 1 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.47616 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.33151 | 7.367 | 0 | 0 | 0
1 | 1 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.87891 | 100 | 1.5 | 100 | 2 | 100 | 1.4063 | 95.1784 | 0 | 0 | 0 | 0 | 0
1 | 1 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1825 | 100 | 1.5 | 100 | 2 | 100 | 1.1027 | 74.6335 | 0 | 0 | 0 | 0 | 0
1 | 1 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3789 | 100 | 1.5 | 100 | 2 | 100 | 0.90629 | 61.3397 | 0 | 0 | 0 | 0 | 0
1 | 1 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4523 | 100 | 1.5 | 100 | 2 | 100 | 0.83289 | 56.3713 | 0 | 0 | 0 | 0 | 0
1 | 1 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3967 | 100 | 1.5 | 100 | 2 | 100 | 0.88844 | 60.1311 | 0 | 0 | 0 | 0 | 0
1 | 1 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.2241 | 100 | 1.5 | 100 | 2 | 100 | 1.061 | 71.8136 | 0 | 0 | 0 | 0 | 0
1 | 1 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.93446 | 100 | 1.5 | 100 | 2 | 100 | 1.3507 | 91.4186 | 0 | 0 | 0 | 0 | 0
1 | 1 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.56346 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.24422 | 5.4271 | 0 | 0 | 0
1 | 1 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.07936 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.72831 | 16.1847 | 0 | 0 | 0
1 | 1 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 1 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 1 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 1 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 1 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 1 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 2 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 2 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 2 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 2 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 2 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 2 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 2 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 2 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.071424 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.73625 | 16.3611 | 0 | 0 | 0
1 | 2 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.51981 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.28787 | 6.397 | 0 | 0 | 0
1 | 2 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.92256 | 100 | 1.5 | 100 | 2 | 100 | 1.3626 | 92.2243 | 0 | 0 | 0 | 0 | 0
1 | 2 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.238 | 100 | 1.5 | 100 | 2 | 100 | 1.0472 | 70.8736 | 0 | 0 | 0 | 0 | 0
1 | 2 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4503 | 100 | 1.5 | 100 | 2 | 100 | 0.83487 | 56.5056 | 0 | 0 | 0 | 0 | 0
1 | 2 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.5336 | 100 | 1.5 | 100 | 2 | 100 | 0.75154 | 50.8658 | 0 | 0 | 0 | 0 | 0
1 | 2 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.494 | 100 | 1.5 | 100 | 2 | 100 | 0.79122 | 53.5514 | 0 | 0 | 0 | 0 | 0
1 | 2 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3293 | 100 | 1.5 | 100 | 2 | 100 | 0.95589 | 64.6967 | 0 | 0 | 0 | 0 | 0
1 | 2 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0555 | 100 | 1.5 | 100 | 2 | 100 | 1.2297 | 83.2275 | 0 | 0 | 0 | 0 | 0
1 | 2 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.68845 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.11923 | 2.6495 | 0 | 0 | 0
1 | 2 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.18054 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.62713 | 13.9362 | 0 | 0 | 0
1 | 2 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 2 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 2 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 2 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 2 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 2 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 3 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 3 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 3 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 3 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 3 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 3 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 3 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.001984 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80569 | 17.9042 | 0 | 0 | 0
1 | 3 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.16467 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.643 | 14.2889 | 0 | 0 | 0
1 | 3 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.59718 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.21049 | 4.6775 | 0 | 0 | 0
1 | 3 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.98406 | 100 | 1.5 | 100 | 2 | 100 | 1.3011 | 88.0616 | 0 | 0 | 0 | 0 | 0
1 | 3 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.2737 | 100 | 1.5 | 100 | 2 | 100 | 1.0114 | 68.4566 | 0 | 0 | 0 | 0 | 0
1 | 3 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4741 | 100 | 1.5 | 100 | 2 | 100 | 0.81106 | 54.8942 | 0 | 0 | 0 | 0 | 0
1 | 3 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.5495 | 100 | 1.5 | 100 | 2 | 100 | 0.73567 | 49.7915 | 0 | 0 | 0 | 0 | 0
1 | 3 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.5138 | 100 | 1.5 | 100 | 2 | 100 | 0.77138 | 52.2086 | 0 | 0 | 0 | 0 | 0
1 | 3 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3114 | 100 | 1.5 | 100 | 2 | 100 | 0.97375 | 65.9052 | 0 | 0 | 0 | 0 | 0
1 | 3 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0396 | 100 | 1.5 | 100 | 2 | 100 | 1.2456 | 84.3017 | 0 | 0 | 0 | 0 | 0
1 | 3 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.68051 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.12716 | 2.8258 | 0 | 0 | 0
1 | 3 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.25594 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.55174 | 12.2608 | 0 | 0 | 0
1 | 3 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.001984 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80569 | 17.9042 | 0 | 0 | 0
1 | 3 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 3 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 3 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 3 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 3 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 4 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 4 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 4 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 4 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 4 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 4 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 4 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.02976 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.77791 | 17.287 | 0 | 0 | 0
1 | 4 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.28768 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.51999 | 11.5554 | 0 | 0 | 0
1 | 4 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.66266 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.14502 | 3.2226 | 0 | 0 | 0
1 | 4 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0079 | 100 | 1.5 | 100 | 2 | 100 | 1.2773 | 86.4502 | 0 | 0 | 0 | 0 | 0
1 | 4 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.2678 | 100 | 1.5 | 100 | 2 | 100 | 1.0174 | 68.8594 | 0 | 0 | 0 | 0 | 0
1 | 4 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4265 | 100 | 1.5 | 100 | 2 | 100 | 0.85868 | 58.1169 | 0 | 0 | 0 | 0 | 0
1 | 4 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4761 | 100 | 1.5 | 100 | 2 | 100 | 0.80908 | 54.7599 | 0 | 0 | 0 | 0 | 0
1 | 4 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4027 | 100 | 1.5 | 100 | 2 | 100 | 0.88249 | 59.7283 | 0 | 0 | 0 | 0 | 0
1 | 4 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.2261 | 100 | 1.5 | 100 | 2 | 100 | 1.0591 | 71.6793 | 0 | 0 | 0 | 0 | 0
1 | 4 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.95232 | 100 | 1.5 | 100 | 2 | 100 | 1.3329 | 90.2101 | 0 | 0 | 0 | 0 | 0
1 | 4 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.62298 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.1847 | 4.1044 | 0 | 0 | 0
1 | 4 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.26189 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.54579 | 12.1286 | 0 | 0 | 0
1 | 4 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.01984 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.78783 | 17.5074 | 0 | 0 | 0
1 | 4 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 4 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 4 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 4 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 4 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 5 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 5 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 5 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 5 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 5 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 5 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 5 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.071424 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.73625 | 16.3611 | 0 | 0 | 0
1 | 5 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.31744 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.49023 | 10.8941 | 0 | 0 | 0
1 | 5 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.64678 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.16089 | 3.5753 | 0 | 0 | 0
1 | 5 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.95629 | 100 | 1.5 | 100 | 2 | 100 | 1.3289 | 89.9415 | 0 | 0 | 0 | 0 | 0
1 | 5 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1904 | 100 | 1.5 | 100 | 2 | 100 | 1.0948 | 74.0964 | 0 | 0 | 0 | 0 | 0
1 | 5 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3352 | 100 | 1.5 | 100 | 2 | 100 | 0.94994 | 64.2938 | 0 | 0 | 0 | 0 | 0
1 | 5 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3749 | 100 | 1.5 | 100 | 2 | 100 | 0.91026 | 61.6082 | 0 | 0 | 0 | 0 | 0
1 | 5 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3055 | 100 | 1.5 | 100 | 2 | 100 | 0.9797 | 66.3081 | 0 | 0 | 0 | 0 | 0
1 | 5 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1388 | 100 | 1.5 | 100 | 2 | 100 | 1.1464 | 77.5877 | 0 | 0 | 0 | 0 | 0
1 | 5 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.88685 | 100 | 1.5 | 100 | 2 | 100 | 1.3983 | 94.6413 | 0 | 0 | 0 | 0 | 0
1 | 5 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.57536 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.23231 | 5.1625 | 0 | 0 | 0
1 | 5 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.26586 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.54182 | 12.0404 | 0 | 0 | 0
1 | 5 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.037696 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.76998 | 17.1106 | 0 | 0 | 0
1 | 5 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 5 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 5 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 5 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 5 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 6 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 6 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 6 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 6 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 6 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 6 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 6 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.06944 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.73823 | 16.4052 | 0 | 0 | 0
1 | 6 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.26189 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.54579 | 12.1286 | 0 | 0 | 0
1 | 6 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.53766 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.27001 | 6.0002 | 0 | 0 | 0
1 | 6 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.82138 | 100 | 1.5 | 100 | 2 | 100 | 1.4638 | 99.0726 | 0 | 0 | 0 | 0 | 0
1 | 6 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0456 | 100 | 1.5 | 100 | 2 | 100 | 1.2396 | 83.8989 | 0 | 0 | 0 | 0 | 0
1 | 6 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1805 | 100 | 1.5 | 100 | 2 | 100 | 1.1047 | 74.7678 | 0 | 0 | 0 | 0 | 0
1 | 6 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.236 | 100 | 1.5 | 100 | 2 | 100 | 1.0491 | 71.0079 | 0 | 0 | 0 | 0 | 0
1 | 6 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1785 | 100 | 1.5 | 100 | 2 | 100 | 1.1067 | 74.902 | 0 | 0 | 0 | 0 | 0
1 | 6 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0277 | 100 | 1.5 | 100 | 2 | 100 | 1.2575 | 85.1074 | 0 | 0 | 0 | 0 | 0
1 | 6 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.81344 | 100 | 1.5 | 100 | 2 | 100 | 1.4717 | 99.6097 | 0 | 0 | 0 | 0 | 0
1 | 6 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.54362 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.26406 | 5.8679 | 0 | 0 | 0
1 | 6 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.26784 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.53983 | 11.9963 | 0 | 0 | 0
1 | 6 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.055552 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.75212 | 16.7138 | 0 | 0 | 0
1 | 6 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 6 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 6 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 6 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 6 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 7 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 7 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 7 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 7 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 7 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 7 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 7 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.037696 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.76998 | 17.1106 | 0 | 0 | 0
1 | 7 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.19443 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.61324 | 13.6276 | 0 | 0 | 0
1 | 7 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.42259 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.38508 | 8.5574 | 0 | 0 | 0
1 | 7 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.66861 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.13907 | 3.0903 | 0 | 0 | 0
1 | 7 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.87494 | 100 | 1.5 | 100 | 2 | 100 | 1.4102 | 95.447 | 0 | 0 | 0 | 0 | 0
1 | 7 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0218 | 100 | 1.5 | 100 | 2 | 100 | 1.2634 | 85.5102 | 0 | 0 | 0 | 0 | 0
1 | 7 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0753 | 100 | 1.5 | 100 | 2 | 100 | 1.2098 | 81.8846 | 0 | 0 | 0 | 0 | 0
1 | 7 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0416 | 100 | 1.5 | 100 | 2 | 100 | 1.2436 | 84.1674 | 0 | 0 | 0 | 0 | 0
1 | 7 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.92256 | 100 | 1.5 | 100 | 2 | 100 | 1.3626 | 92.2243 | 0 | 0 | 0 | 0 | 0
1 | 7 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.71821 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.089466 | 1.9881 | 0 | 0 | 0
1 | 7 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.48211 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.32556 | 7.2347 | 0 | 0 | 0
1 | 7 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.24602 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.56166 | 12.4813 | 0 | 0 | 0
1 | 7 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.057536 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.75014 | 16.6697 | 0 | 0 | 0
1 | 7 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 7 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 7 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 7 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 7 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 8 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 8 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 8 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 8 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 8 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 8 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 8 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.021824 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.78585 | 17.4633 | 0 | 0 | 0
1 | 8 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.20038 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.60729 | 13.4953 | 0 | 0 | 0
1 | 8 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.46029 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.34739 | 7.7197 | 0 | 0 | 0
1 | 8 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.72813 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.079546 | 1.7677 | 0 | 0 | 0
1 | 8 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.95232 | 100 | 1.5 | 100 | 2 | 100 | 1.3329 | 90.2101 | 0 | 0 | 0 | 0 | 0
1 | 8 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1051 | 100 | 1.5 | 100 | 2 | 100 | 1.1801 | 79.8704 | 0 | 0 | 0 | 0 | 0
1 | 8 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1686 | 100 | 1.5 | 100 | 2 | 100 | 1.1166 | 75.5734 | 0 | 0 | 0 | 0 | 0
1 | 8 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.113 | 100 | 1.5 | 100 | 2 | 100 | 1.1721 | 79.3333 | 0 | 0 | 0 | 0 | 0
1 | 8 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.98208 | 100 | 1.5 | 100 | 2 | 100 | 1.3031 | 88.1958 | 0 | 0 | 0 | 0 | 0
1 | 8 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.75987 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.047802 | 1.0623 | 0 | 0 | 0
1 | 8 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.496 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.31167 | 6.9261 | 0 | 0 | 0
1 | 8 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.22816 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.57951 | 12.8781 | 0 | 0 | 0
1 | 8 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.027776 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.7799 | 17.3311 | 0 | 0 | 0
1 | 8 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 8 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 8 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 8 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 8 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 9 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 9 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 9 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 9 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 9 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 9 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 9 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.017856 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.78982 | 17.5515 | 0 | 0 | 0
1 | 9 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.25792 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.54975 | 12.2167 | 0 | 0 | 0
1 | 9 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.61504 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.19263 | 4.2807 | 0 | 0 | 0
1 | 9 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.9424 | 100 | 1.5 | 100 | 2 | 100 | 1.3428 | 90.8815 | 0 | 0 | 0 | 0 | 0
1 | 9 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1904 | 100 | 1.5 | 100 | 2 | 100 | 1.0948 | 74.0964 | 0 | 0 | 0 | 0 | 0
1 | 9 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3452 | 100 | 1.5 | 100 | 2 | 100 | 0.94002 | 63.6224 | 0 | 0 | 0 | 0 | 0
1 | 9 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3908 | 100 | 1.5 | 100 | 2 | 100 | 0.89439 | 60.534 | 0 | 0 | 0 | 0 | 0
1 | 9 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3114 | 100 | 1.5 | 100 | 2 | 100 | 0.97375 | 65.9052 | 0 | 0 | 0 | 0 | 0
1 | 9 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.117 | 100 | 1.5 | 100 | 2 | 100 | 1.1682 | 79.0647 | 0 | 0 | 0 | 0 | 0
1 | 9 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.85709 | 100 | 1.5 | 100 | 2 | 100 | 1.4281 | 96.6555 | 0 | 0 | 0 | 0 | 0
1 | 9 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.52378 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.2839 | 6.3088 | 0 | 0 | 0
1 | 9 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.17062 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.63705 | 14.1567 | 0 | 0 | 0
1 | 9 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.001984 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80569 | 17.9042 | 0 | 0 | 0
1 | 9 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 9 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 9 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 9 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 9 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 10 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 10 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 10 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 10 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 10 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 10 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 10 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 10 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.27181 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.53587 | 11.9081 | 0 | 0 | 0
1 | 10 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.72614 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.08153 | 1.8118 | 0 | 0 | 0
1 | 10 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0753 | 100 | 1.5 | 100 | 2 | 100 | 1.2098 | 81.8846 | 0 | 0 | 0 | 0 | 0
1 | 10 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3273 | 100 | 1.5 | 100 | 2 | 100 | 0.95788 | 64.831 | 0 | 0 | 0 | 0 | 0
1 | 10 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4721 | 100 | 1.5 | 100 | 2 | 100 | 0.81305 | 55.0285 | 0 | 0 | 0 | 0 | 0
1 | 10 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4959 | 100 | 1.5 | 100 | 2 | 100 | 0.78924 | 53.4171 | 0 | 0 | 0 | 0 | 0
1 | 10 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3789 | 100 | 1.5 | 100 | 2 | 100 | 0.90629 | 61.3397 | 0 | 0 | 0 | 0 | 0
1 | 10 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1567 | 100 | 1.5 | 100 | 2 | 100 | 1.1285 | 76.3791 | 0 | 0 | 0 | 0 | 0
1 | 10 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.84717 | 100 | 1.5 | 100 | 2 | 100 | 1.438 | 97.3269 | 0 | 0 | 0 | 0 | 0
1 | 10 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.47418 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.3335 | 7.4111 | 0 | 0 | 0
1 | 10 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.061504 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.74617 | 16.5815 | 0 | 0 | 0
1 | 10 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 10 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 10 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 10 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 10 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 10 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 11 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 11 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 11 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 11 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 11 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 11 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 11 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 11 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.1607 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.64697 | 14.3771 | 0 | 0 | 0
1 | 11 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.65274 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.15494 | 3.4431 | 0 | 0 | 0
1 | 11 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.0218 | 100 | 1.5 | 100 | 2 | 100 | 1.2634 | 85.5102 | 0 | 0 | 0 | 0 | 0
1 | 11 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.2777 | 100 | 1.5 | 100 | 2 | 100 | 1.0075 | 68.188 | 0 | 0 | 0 | 0 | 0
1 | 11 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4186 | 100 | 1.5 | 100 | 2 | 100 | 0.86661 | 58.654 | 0 | 0 | 0 | 0 | 0
1 | 11 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4324 | 100 | 1.5 | 100 | 2 | 100 | 0.85273 | 57.7141 | 0 | 0 | 0 | 0 | 0
1 | 11 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3332 | 100 | 1.5 | 100 | 2 | 100 | 0.95193 | 64.4281 | 0 | 0 | 0 | 0 | 0
1 | 11 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.111 | 100 | 1.5 | 100 | 2 | 100 | 1.1741 | 79.4676 | 0 | 0 | 0 | 0 | 0
1 | 11 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.79757 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.010106 | 0.22457 | 0 | 0 | 0
1 | 11 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.3472 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.46047 | 10.2327 | 0 | 0 | 0
1 | 11 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 11 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 11 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 11 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 11 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 11 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 11 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 12 | 1 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 12 | 2 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 12 | 3 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 12 | 4 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 12 | 5 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 12 | 6 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 12 | 7 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 12 | 8 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.065472 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.7422 | 16.4934 | 0 | 0 | 0
1 | 12 | 9 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.54163 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.26604 | 5.912 | 0 | 0 | 0
1 | 12 | 10 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.92653 | 100 | 1.5 | 100 | 2 | 100 | 1.3586 | 91.9557 | 0 | 0 | 0 | 0 | 0
1 | 12 | 11 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.2023 | 100 | 1.5 | 100 | 2 | 100 | 1.0829 | 73.2907 | 0 | 0 | 0 | 0 | 0
1 | 12 | 12 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3709 | 100 | 1.5 | 100 | 2 | 100 | 0.91423 | 61.8768 | 0 | 0 | 0 | 0 | 0
1 | 12 | 13 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.4166 | 100 | 1.5 | 100 | 2 | 100 | 0.8686 | 58.7883 | 0 | 0 | 0 | 0 | 0
1 | 12 | 14 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.3313 | 100 | 1.5 | 100 | 2 | 100 | 0.95391 | 64.5624 | 0 | 0 | 0 | 0 | 0
1 | 12 | 15 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 1.1269 | 100 | 1.5 | 100 | 2 | 100 | 1.1583 | 78.3933 | 0 | 0 | 0 | 0 | 0
1 | 12 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.8313 | 100 | 1.5 | 100 | 2 | 100 | 1.4539 | 98.4012 | 0 | 0 | 0 | 0 | 0
1 | 12 | 17 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.38291 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.42476 | 9.4391 | 0 | 0 | 0
1 | 12 | 18 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.003968 | 100 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80371 | 17.8601 | 0 | 0 | 0
1 | 12 | 19 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 12 | 20 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 12 | 21 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 12 | 22 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 12 | 23 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
1 | 12 | 24 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.4775 | 100 | 0.80767 | 17.9483 | 0 | 0 | 0
2 | 1 | 1 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 1 | 2 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 1 | 3 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 1 | 4 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 1 | 5 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 1 | 6 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 1 | 7 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 1 | 8 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.043296 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.79102 | 17.5783 | 0 | 0 | 0
2 | 1 | 9 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.47232 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.362 | 8.0444 | 0 | 0 | 0
2 | 1 | 10 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.87182 | 100 | 1.5 | 100 | 2 | 100 | 1.4175 | 97.4223 | 0 | 0 | 0 | 0 | 0
2 | 1 | 11 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.1729 | 100 | 1.5 | 100 | 2 | 100 | 1.1164 | 76.7279 | 0 | 0 | 0 | 0 | 0
2 | 1 | 12 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.3678 | 100 | 1.5 | 100 | 2 | 100 | 0.92156 | 63.3374 | 0 | 0 | 0 | 0 | 0
2 | 1 | 13 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.4406 | 100 | 1.5 | 100 | 2 | 100 | 0.84874 | 58.3329 | 0 | 0 | 0 | 0 | 0
2 | 1 | 14 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.3855 | 100 | 1.5 | 100 | 2 | 100 | 0.90385 | 62.1201 | 0 | 0 | 0 | 0 | 0
2 | 1 | 15 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.2143 | 100 | 1.5 | 100 | 2 | 100 | 1.0751 | 73.8875 | 0 | 0 | 0 | 0 | 0
2 | 1 | 16 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.92693 | 100 | 1.5 | 100 | 2 | 100 | 1.3624 | 93.6351 | 0 | 0 | 0 | 0 | 0
2 | 1 | 17 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.55891 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.27541 | 6.1202 | 0 | 0 | 0
2 | 1 | 18 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.07872 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.7556 | 16.7911 | 0 | 0 | 0
2 | 1 | 19 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 1 | 20 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 1 | 21 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 1 | 22 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 1 | 23 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 1 | 24 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 2 | 1 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 2 | 2 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 2 | 3 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 2 | 4 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 2 | 5 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 2 | 6 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 2 | 7 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 2 | 8 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.070848 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.76347 | 16.966 | 0 | 0 | 0
2 | 2 | 9 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.51562 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.3187 | 7.0823 | 0 | 0 | 0
2 | 2 | 10 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.91512 | 100 | 1.5 | 100 | 2 | 100 | 1.3742 | 94.4467 | 0 | 0 | 0 | 0 | 0
2 | 2 | 11 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.228 | 100 | 1.5 | 100 | 2 | 100 | 1.0613 | 72.9407 | 0 | 0 | 0 | 0 | 0
2 | 2 | 12 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.4386 | 100 | 1.5 | 100 | 2 | 100 | 0.85071 | 58.4681 | 0 | 0 | 0 | 0 | 0
2 | 2 | 13 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.5213 | 100 | 1.5 | 100 | 2 | 100 | 0.76806 | 52.7873 | 0 | 0 | 0 | 0 | 0
2 | 2 | 14 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.4819 | 100 | 1.5 | 100 | 2 | 100 | 0.80742 | 55.4925 | 0 | 0 | 0 | 0 | 0
2 | 2 | 15 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.3186 | 100 | 1.5 | 100 | 2 | 100 | 0.97076 | 66.7188 | 0 | 0 | 0 | 0 | 0
2 | 2 | 16 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.047 | 100 | 1.5 | 100 | 2 | 100 | 1.2423 | 85.3844 | 0 | 0 | 0 | 0 | 0
2 | 2 | 17 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.6829 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.15142 | 3.365 | 0 | 0 | 0
2 | 2 | 18 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.17909 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.65523 | 14.5607 | 0 | 0 | 0
2 | 2 | 19 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 2 | 20 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 2 | 21 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 2 | 22 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 2 | 23 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 2 | 24 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 3 | 1 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 3 | 2 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 3 | 3 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 3 | 4 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 3 | 5 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 3 | 6 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 3 | 7 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.001968 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83235 | 18.4967 | 0 | 0 | 0
2 | 3 | 8 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.16334 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.67098 | 14.9106 | 0 | 0 | 0
2 | 3 | 9 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.59237 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.24195 | 5.3767 | 0 | 0 | 0
2 | 3 | 10 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.97613 | 100 | 1.5 | 100 | 2 | 100 | 1.3132 | 90.2537 | 0 | 0 | 0 | 0 | 0
2 | 3 | 11 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.2635 | 100 | 1.5 | 100 | 2 | 100 | 1.0259 | 70.5061 | 0 | 0 | 0 | 0 | 0
2 | 3 | 12 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.4622 | 100 | 1.5 | 100 | 2 | 100 | 0.8271 | 56.845 | 0 | 0 | 0 | 0 | 0
2 | 3 | 13 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.537 | 100 | 1.5 | 100 | 2 | 100 | 0.75231 | 51.7052 | 0 | 0 | 0 | 0 | 0
2 | 3 | 14 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.5016 | 100 | 1.5 | 100 | 2 | 100 | 0.78774 | 54.1399 | 0 | 0 | 0 | 0 | 0
2 | 3 | 15 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.3008 | 100 | 1.5 | 100 | 2 | 100 | 0.98847 | 67.9362 | 0 | 0 | 0 | 0 | 0
2 | 3 | 16 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.0312 | 100 | 1.5 | 100 | 2 | 100 | 1.2581 | 86.4665 | 0 | 0 | 0 | 0 | 0
2 | 3 | 17 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.67502 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.1593 | 3.5399 | 0 | 0 | 0
2 | 3 | 18 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.25387 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.58045 | 12.8988 | 0 | 0 | 0
2 | 3 | 19 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.001968 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83235 | 18.4967 | 0 | 0 | 0
2 | 3 | 20 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 3 | 21 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 3 | 22 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 3 | 23 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 3 | 24 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 4 | 1 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 4 | 2 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 4 | 3 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 4 | 4 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 4 | 5 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 4 | 6 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 4 | 7 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.02952 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.8048 | 17.8844 | 0 | 0 | 0
2 | 4 | 8 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.28536 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.54896 | 12.1991 | 0 | 0 | 0
2 | 4 | 9 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.65731 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.17701 | 3.9335 | 0 | 0 | 0
2 | 4 | 10 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.99974 | 100 | 1.5 | 100 | 2 | 100 | 1.2896 | 88.6306 | 0 | 0 | 0 | 0 | 0
2 | 4 | 11 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.2576 | 100 | 1.5 | 100 | 2 | 100 | 1.0318 | 70.9118 | 0 | 0 | 0 | 0 | 0
2 | 4 | 12 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.415 | 100 | 1.5 | 100 | 2 | 100 | 0.87433 | 60.0912 | 0 | 0 | 0 | 0 | 0
2 | 4 | 13 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.4642 | 100 | 1.5 | 100 | 2 | 100 | 0.82513 | 56.7098 | 0 | 0 | 0 | 0 | 0
2 | 4 | 14 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.3914 | 100 | 1.5 | 100 | 2 | 100 | 0.89794 | 61.7143 | 0 | 0 | 0 | 0 | 0
2 | 4 | 15 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.2162 | 100 | 1.5 | 100 | 2 | 100 | 1.0731 | 73.7522 | 0 | 0 | 0 | 0 | 0
2 | 4 | 16 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.94464 | 100 | 1.5 | 100 | 2 | 100 | 1.3447 | 92.4178 | 0 | 0 | 0 | 0 | 0
2 | 4 | 17 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.61795 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.21637 | 4.8082 | 0 | 0 | 0
2 | 4 | 18 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.25978 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.57454 | 12.7676 | 0 | 0 | 0
2 | 4 | 19 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.01968 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.81464 | 18.1031 | 0 | 0 | 0
2 | 4 | 20 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 4 | 21 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 4 | 22 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 4 | 23 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 4 | 24 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 5 | 1 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 5 | 2 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 5 | 3 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 5 | 4 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 5 | 5 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 5 | 6 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 5 | 7 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.070848 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.76347 | 16.966 | 0 | 0 | 0
2 | 5 | 8 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.31488 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.51944 | 11.5431 | 0 | 0 | 0
2 | 5 | 9 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.64157 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.19275 | 4.2834 | 0 | 0 | 0
2 | 5 | 10 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.94858 | 100 | 1.5 | 100 | 2 | 100 | 1.3407 | 92.1473 | 0 | 0 | 0 | 0 | 0
2 | 5 | 11 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.1808 | 100 | 1.5 | 100 | 2 | 100 | 1.1085 | 76.1869 | 0 | 0 | 0 | 0 | 0
2 | 5 | 12 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.3245 | 100 | 1.5 | 100 | 2 | 100 | 0.96486 | 66.3131 | 0 | 0 | 0 | 0 | 0
2 | 5 | 13 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.3638 | 100 | 1.5 | 100 | 2 | 100 | 0.9255 | 63.6079 | 0 | 0 | 0 | 0 | 0
2 | 5 | 14 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.2949 | 100 | 1.5 | 100 | 2 | 100 | 0.99438 | 68.3419 | 0 | 0 | 0 | 0 | 0
2 | 5 | 15 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.1296 | 100 | 1.5 | 100 | 2 | 100 | 1.1597 | 79.7036 | 0 | 0 | 0 | 0 | 0
2 | 5 | 16 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.8797 | 100 | 1.5 | 100 | 2 | 100 | 1.4096 | 96.8813 | 0 | 0 | 0 | 0 | 0
2 | 5 | 17 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.57072 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.2636 | 5.8578 | 0 | 0 | 0
2 | 5 | 18 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.26371 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.57061 | 12.6802 | 0 | 0 | 0
2 | 5 | 19 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.037392 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.79693 | 17.7095 | 0 | 0 | 0
2 | 5 | 20 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 5 | 21 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 5 | 22 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 5 | 23 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 5 | 24 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 6 | 1 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 6 | 2 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 6 | 3 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 6 | 4 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 6 | 5 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 6 | 6 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 6 | 7 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.06888 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.76544 | 17.0098 | 0 | 0 | 0
2 | 6 | 8 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.25978 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.57454 | 12.7676 | 0 | 0 | 0
2 | 6 | 9 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.53333 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.30099 | 6.6887 | 0 | 0 | 0
2 | 6 | 10 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.81475 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.019567 | 0.43483 | 0 | 0 | 0
2 | 6 | 11 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.0371 | 100 | 1.5 | 100 | 2 | 100 | 1.2522 | 86.0607 | 0 | 0 | 0 | 0 | 0
2 | 6 | 12 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.171 | 100 | 1.5 | 100 | 2 | 100 | 1.1184 | 76.8632 | 0 | 0 | 0 | 0 | 0
2 | 6 | 13 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.2261 | 100 | 1.5 | 100 | 2 | 100 | 1.0633 | 73.076 | 0 | 0 | 0 | 0 | 0
2 | 6 | 14 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.169 | 100 | 1.5 | 100 | 2 | 100 | 1.1203 | 76.9984 | 0 | 0 | 0 | 0 | 0
2 | 6 | 15 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.0194 | 100 | 1.5 | 100 | 2 | 100 | 1.2699 | 87.278 | 0 | 0 | 0 | 0 | 0
2 | 6 | 16 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.80688 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.027439 | 0.60976 | 0 | 0 | 0
2 | 6 | 17 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.53923 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.29509 | 6.5575 | 0 | 0 | 0
2 | 6 | 18 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.26568 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.56864 | 12.6364 | 0 | 0 | 0
2 | 6 | 19 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.055104 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.77922 | 17.3159 | 0 | 0 | 0
2 | 6 | 20 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 6 | 21 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 6 | 22 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 6 | 23 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 6 | 24 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 7 | 1 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 7 | 2 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 7 | 3 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 7 | 4 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 7 | 5 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 7 | 6 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 7 | 7 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.037392 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.79693 | 17.7095 | 0 | 0 | 0
2 | 7 | 8 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.19286 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.64146 | 14.2546 | 0 | 0 | 0
2 | 7 | 9 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.41918 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.41514 | 9.2252 | 0 | 0 | 0
2 | 7 | 10 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.66322 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.1711 | 3.8023 | 0 | 0 | 0
2 | 7 | 11 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.86789 | 100 | 1.5 | 100 | 2 | 100 | 1.4214 | 97.6929 | 0 | 0 | 0 | 0 | 0
2 | 7 | 12 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.0135 | 100 | 1.5 | 100 | 2 | 100 | 1.2758 | 87.6838 | 0 | 0 | 0 | 0 | 0
2 | 7 | 13 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.0667 | 100 | 1.5 | 100 | 2 | 100 | 1.2227 | 84.0318 | 0 | 0 | 0 | 0 | 0
2 | 7 | 14 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.0332 | 100 | 1.5 | 100 | 2 | 100 | 1.2561 | 86.3312 | 0 | 0 | 0 | 0 | 0
2 | 7 | 15 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.91512 | 100 | 1.5 | 100 | 2 | 100 | 1.3742 | 94.4467 | 0 | 0 | 0 | 0 | 0
2 | 7 | 16 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.71242 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.1219 | 2.709 | 0 | 0 | 0
2 | 7 | 17 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.47822 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.3561 | 7.9132 | 0 | 0 | 0
2 | 7 | 18 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.24403 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.59029 | 13.1175 | 0 | 0 | 0
2 | 7 | 19 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.057072 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.77725 | 17.2722 | 0 | 0 | 0
2 | 7 | 20 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 7 | 21 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 7 | 22 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 7 | 23 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 7 | 24 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 8 | 1 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 8 | 2 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 8 | 3 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 8 | 4 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 8 | 5 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 8 | 6 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 8 | 7 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.021648 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.81267 | 18.0594 | 0 | 0 | 0
2 | 8 | 8 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.19877 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.63555 | 14.1234 | 0 | 0 | 0
2 | 8 | 9 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.45658 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.37774 | 8.3943 | 0 | 0 | 0
2 | 8 | 10 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.72226 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.11206 | 2.4903 | 0 | 0 | 0
2 | 8 | 11 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.94464 | 100 | 1.5 | 100 | 2 | 100 | 1.3447 | 92.4178 | 0 | 0 | 0 | 0 | 0
2 | 8 | 12 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.0962 | 100 | 1.5 | 100 | 2 | 100 | 1.1931 | 82.003 | 0 | 0 | 0 | 0 | 0
2 | 8 | 13 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.1592 | 100 | 1.5 | 100 | 2 | 100 | 1.1302 | 77.6747 | 0 | 0 | 0 | 0 | 0
2 | 8 | 14 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.104 | 100 | 1.5 | 100 | 2 | 100 | 1.1853 | 81.4619 | 0 | 0 | 0 | 0 | 0
2 | 8 | 15 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.97416 | 100 | 1.5 | 100 | 2 | 100 | 1.3152 | 90.3889 | 0 | 0 | 0 | 0 | 0
2 | 8 | 16 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.75374 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.080575 | 1.7906 | 0 | 0 | 0
2 | 8 | 17 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.492 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.34232 | 7.6071 | 0 | 0 | 0
2 | 8 | 18 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.22632 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.608 | 13.5111 | 0 | 0 | 0
2 | 8 | 19 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.027552 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.80677 | 17.9282 | 0 | 0 | 0
2 | 8 | 20 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 8 | 21 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 8 | 22 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 8 | 23 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 8 | 24 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 9 | 1 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 9 | 2 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 9 | 3 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 9 | 4 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 9 | 5 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 9 | 6 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 9 | 7 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.017712 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.81661 | 18.1468 | 0 | 0 | 0
2 | 9 | 8 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.25584 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.57848 | 12.8551 | 0 | 0 | 0
2 | 9 | 9 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.61008 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.22424 | 4.9831 | 0 | 0 | 0
2 | 9 | 10 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.9348 | 100 | 1.5 | 100 | 2 | 100 | 1.3545 | 93.0941 | 0 | 0 | 0 | 0 | 0
2 | 9 | 11 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.1808 | 100 | 1.5 | 100 | 2 | 100 | 1.1085 | 76.1869 | 0 | 0 | 0 | 0 | 0
2 | 9 | 12 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.3343 | 100 | 1.5 | 100 | 2 | 100 | 0.95502 | 65.6368 | 0 | 0 | 0 | 0 | 0
2 | 9 | 13 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.3796 | 100 | 1.5 | 100 | 2 | 100 | 0.90975 | 62.5259 | 0 | 0 | 0 | 0 | 0
2 | 9 | 14 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.3008 | 100 | 1.5 | 100 | 2 | 100 | 0.98847 | 67.9362 | 0 | 0 | 0 | 0 | 0
2 | 9 | 15 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.108 | 100 | 1.5 | 100 | 2 | 100 | 1.1813 | 81.1914 | 0 | 0 | 0 | 0 | 0
2 | 9 | 16 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.85018 | 100 | 1.5 | 100 | 2 | 100 | 1.4391 | 98.9102 | 0 | 0 | 0 | 0 | 0
2 | 9 | 17 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.51955 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.31477 | 6.9948 | 0 | 0 | 0
2 | 9 | 18 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.16925 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.66507 | 14.7794 | 0 | 0 | 0
2 | 9 | 19 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.001968 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83235 | 18.4967 | 0 | 0 | 0
2 | 9 | 20 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 9 | 21 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 9 | 22 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 9 | 23 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 9 | 24 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 10 | 1 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 10 | 2 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 10 | 3 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 10 | 4 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 10 | 5 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 10 | 6 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 10 | 7 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 10 | 8 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.26962 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.5647 | 12.549 | 0 | 0 | 0
2 | 10 | 9 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.72029 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.11403 | 2.534 | 0 | 0 | 0
2 | 10 | 10 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.0667 | 100 | 1.5 | 100 | 2 | 100 | 1.2227 | 84.0318 | 0 | 0 | 0 | 0 | 0
2 | 10 | 11 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.3166 | 100 | 1.5 | 100 | 2 | 100 | 0.97273 | 66.8541 | 0 | 0 | 0 | 0 | 0
2 | 10 | 12 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.4603 | 100 | 1.5 | 100 | 2 | 100 | 0.82906 | 56.9803 | 0 | 0 | 0 | 0 | 0
2 | 10 | 13 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.4839 | 100 | 1.5 | 100 | 2 | 100 | 0.80545 | 55.3572 | 0 | 0 | 0 | 0 | 0
2 | 10 | 14 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.3678 | 100 | 1.5 | 100 | 2 | 100 | 0.92156 | 63.3374 | 0 | 0 | 0 | 0 | 0
2 | 10 | 15 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.1473 | 100 | 1.5 | 100 | 2 | 100 | 1.142 | 78.4863 | 0 | 0 | 0 | 0 | 0
2 | 10 | 16 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.84034 | 100 | 1.5 | 100 | 2 | 100 | 1.449 | 99.5865 | 0 | 0 | 0 | 0 | 0
2 | 10 | 17 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.47035 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.36397 | 8.0882 | 0 | 0 | 0
2 | 10 | 18 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.061008 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.77331 | 17.1847 | 0 | 0 | 0
2 | 10 | 19 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 10 | 20 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 10 | 21 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 10 | 22 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 10 | 23 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 10 | 24 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 11 | 1 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 11 | 2 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 11 | 3 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 11 | 4 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 11 | 5 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 11 | 6 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 11 | 7 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 11 | 8 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.15941 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.67491 | 14.998 | 0 | 0 | 0
2 | 11 | 9 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.64747 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.18685 | 4.1522 | 0 | 0 | 0
2 | 11 | 10 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.0135 | 100 | 1.5 | 100 | 2 | 100 | 1.2758 | 87.6838 | 0 | 0 | 0 | 0 | 0
2 | 11 | 11 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.2674 | 100 | 1.5 | 100 | 2 | 100 | 1.0219 | 70.2355 | 0 | 0 | 0 | 0 | 0
2 | 11 | 12 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.4071 | 100 | 1.5 | 100 | 2 | 100 | 0.8822 | 60.6322 | 0 | 0 | 0 | 0 | 0
2 | 11 | 13 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.4209 | 100 | 1.5 | 100 | 2 | 100 | 0.86842 | 59.6854 | 0 | 0 | 0 | 0 | 0
2 | 11 | 14 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.3225 | 100 | 1.5 | 100 | 2 | 100 | 0.96682 | 66.4483 | 0 | 0 | 0 | 0 | 0
2 | 11 | 15 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.1021 | 100 | 1.5 | 100 | 2 | 100 | 1.1872 | 81.5972 | 0 | 0 | 0 | 0 | 0
2 | 11 | 16 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.79114 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.043183 | 0.95963 | 0 | 0 | 0
2 | 11 | 17 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.3444 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.48992 | 10.8871 | 0 | 0 | 0
2 | 11 | 18 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 11 | 19 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 11 | 20 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 11 | 21 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 11 | 22 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 11 | 23 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 11 | 24 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 12 | 1 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 12 | 2 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 12 | 3 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 12 | 4 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 12 | 5 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 12 | 6 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 12 | 7 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 12 | 8 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.064944 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.76938 | 17.0972 | 0 | 0 | 0
2 | 12 | 9 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.53726 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.29706 | 6.6012 | 0 | 0 | 0
2 | 12 | 10 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.91906 | 100 | 1.5 | 100 | 2 | 100 | 1.3703 | 94.1762 | 0 | 0 | 0 | 0 | 0
2 | 12 | 11 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.1926 | 100 | 1.5 | 100 | 2 | 100 | 1.0967 | 75.3753 | 0 | 0 | 0 | 0 | 0
2 | 12 | 12 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.3599 | 100 | 1.5 | 100 | 2 | 100 | 0.92943 | 63.8784 | 0 | 0 | 0 | 0 | 0
2 | 12 | 13 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.4052 | 100 | 1.5 | 100 | 2 | 100 | 0.88417 | 60.7675 | 0 | 0 | 0 | 0 | 0
2 | 12 | 14 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.3205 | 100 | 1.5 | 100 | 2 | 100 | 0.96879 | 66.5836 | 0 | 0 | 0 | 0 | 0
2 | 12 | 15 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 1.1178 | 100 | 1.5 | 100 | 2 | 100 | 1.1715 | 80.5151 | 0 | 0 | 0 | 0 | 0
2 | 12 | 16 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.82459 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.0097272 | 0.21616 | 0 | 0 | 0
2 | 12 | 17 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.37982 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.4545 | 10.0999 | 0 | 0 | 0
2 | 12 | 18 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.003936 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83038 | 18.453 | 0 | 0 | 0
2 | 12 | 19 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 12 | 20 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 12 | 21 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 12 | 22 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 12 | 23 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
2 | 12 | 24 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.83432 | 18.5404 | 0 | 0 | 0
3 | 1 | 1 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 1 | 2 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 1 | 3 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 1 | 4 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 1 | 5 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 1 | 6 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 1 | 7 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 1 | 8 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.042944 | 100 | 1.5 | 100 | 2 | 100 | 1.9189 | 59.3619 | 0 | 0 | 0 | 0 | 0
3 | 1 | 9 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.46848 | 100 | 1.5 | 100 | 2 | 100 | 1.4933 | 46.1976 | 0 | 0 | 0 | 0 | 0
3 | 1 | 10 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.86474 | 100 | 1.5 | 100 | 2 | 100 | 1.0971 | 33.9391 | 0 | 0 | 0 | 0 | 0
3 | 1 | 11 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.1634 | 100 | 1.5 | 100 | 2 | 100 | 0.79843 | 24.7 | 0 | 0 | 0 | 0 | 0
3 | 1 | 12 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.3566 | 100 | 1.5 | 100 | 2 | 100 | 0.60518 | 18.7217 | 0 | 0 | 0 | 0 | 0
3 | 1 | 13 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.4289 | 100 | 1.5 | 100 | 2 | 100 | 0.53295 | 16.4874 | 0 | 0 | 0 | 0 | 0
3 | 1 | 14 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.3742 | 100 | 1.5 | 100 | 2 | 100 | 0.58761 | 18.1782 | 0 | 0 | 0 | 0 | 0
3 | 1 | 15 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.2044 | 100 | 1.5 | 100 | 2 | 100 | 0.75743 | 23.4318 | 0 | 0 | 0 | 0 | 0
3 | 1 | 16 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.91939 | 100 | 1.5 | 100 | 2 | 100 | 1.0424 | 32.2483 | 0 | 0 | 0 | 0 | 0
3 | 1 | 17 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.55437 | 100 | 1.5 | 100 | 2 | 100 | 1.4075 | 43.5406 | 0 | 0 | 0 | 0 | 0
3 | 1 | 18 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.07808 | 100 | 1.5 | 100 | 2 | 100 | 1.8837 | 58.275 | 0 | 0 | 0 | 0 | 0
3 | 1 | 19 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 1 | 20 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 1 | 21 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 1 | 22 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 1 | 23 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 1 | 24 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 2 | 1 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 2 | 2 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 2 | 3 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 2 | 4 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 2 | 5 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 2 | 6 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 2 | 7 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 2 | 8 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.070272 | 100 | 1.5 | 100 | 2 | 100 | 1.8915 | 58.5165 | 0 | 0 | 0 | 0 | 0
3 | 2 | 9 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.51142 | 100 | 1.5 | 100 | 2 | 100 | 1.4504 | 44.8691 | 0 | 0 | 0 | 0 | 0
3 | 2 | 10 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.90768 | 100 | 1.5 | 100 | 2 | 100 | 1.0541 | 32.6106 | 0 | 0 | 0 | 0 | 0
3 | 2 | 11 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.218 | 100 | 1.5 | 100 | 2 | 100 | 0.74377 | 23.0091 | 0 | 0 | 0 | 0 | 0
3 | 2 | 12 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.4269 | 100 | 1.5 | 100 | 2 | 100 | 0.53491 | 16.5478 | 0 | 0 | 0 | 0 | 0
3 | 2 | 13 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.5089 | 100 | 1.5 | 100 | 2 | 100 | 0.45292 | 14.0115 | 0 | 0 | 0 | 0 | 0
3 | 2 | 14 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.4699 | 100 | 1.5 | 100 | 2 | 100 | 0.49196 | 15.2193 | 0 | 0 | 0 | 0 | 0
3 | 2 | 15 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.3078 | 100 | 1.5 | 100 | 2 | 100 | 0.65398 | 20.2313 | 0 | 0 | 0 | 0 | 0
3 | 2 | 16 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.0385 | 100 | 1.5 | 100 | 2 | 100 | 0.92335 | 28.5647 | 0 | 0 | 0 | 0 | 0
3 | 2 | 17 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.67734 | 100 | 1.5 | 100 | 2 | 100 | 1.2845 | 39.7363 | 0 | 0 | 0 | 0 | 0
3 | 2 | 18 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.17763 | 100 | 1.5 | 100 | 2 | 100 | 1.7842 | 55.1952 | 0 | 0 | 0 | 0 | 0
3 | 2 | 19 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 2 | 20 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 2 | 21 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 2 | 22 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 2 | 23 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 2 | 24 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 3 | 1 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 3 | 2 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 3 | 3 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 3 | 4 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 3 | 5 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 3 | 6 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 3 | 7 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.001952 | 100 | 1.5 | 100 | 2 | 100 | 1.9599 | 60.63 | 0 | 0 | 0 | 0 | 0
3 | 3 | 8 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.16202 | 100 | 1.5 | 100 | 2 | 100 | 1.7998 | 55.6783 | 0 | 0 | 0 | 0 | 0
3 | 3 | 9 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.58755 | 100 | 1.5 | 100 | 2 | 100 | 1.3743 | 42.514 | 0 | 0 | 0 | 0 | 0
3 | 3 | 10 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.96819 | 100 | 1.5 | 100 | 2 | 100 | 0.99363 | 30.7386 | 0 | 0 | 0 | 0 | 0
3 | 3 | 11 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.2532 | 100 | 1.5 | 100 | 2 | 100 | 0.70863 | 21.9222 | 0 | 0 | 0 | 0 | 0
3 | 3 | 12 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.4503 | 100 | 1.5 | 100 | 2 | 100 | 0.51148 | 15.8231 | 0 | 0 | 0 | 0 | 0
3 | 3 | 13 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.5245 | 100 | 1.5 | 100 | 2 | 100 | 0.43731 | 13.5284 | 0 | 0 | 0 | 0 | 0
3 | 3 | 14 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.4894 | 100 | 1.5 | 100 | 2 | 100 | 0.47244 | 14.6154 | 0 | 0 | 0 | 0 | 0
3 | 3 | 15 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.2903 | 100 | 1.5 | 100 | 2 | 100 | 0.67155 | 20.7748 | 0 | 0 | 0 | 0 | 0
3 | 3 | 16 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.0228 | 100 | 1.5 | 100 | 2 | 100 | 0.93897 | 29.0478 | 0 | 0 | 0 | 0 | 0
3 | 3 | 17 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.66954 | 100 | 1.5 | 100 | 2 | 100 | 1.2923 | 39.9778 | 0 | 0 | 0 | 0 | 0
3 | 3 | 18 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.25181 | 100 | 1.5 | 100 | 2 | 100 | 1.71 | 52.9006 | 0 | 0 | 0 | 0 | 0
3 | 3 | 19 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.001952 | 100 | 1.5 | 100 | 2 | 100 | 1.9599 | 60.63 | 0 | 0 | 0 | 0 | 0
3 | 3 | 20 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 3 | 21 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 3 | 22 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 3 | 23 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 3 | 24 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 4 | 1 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 4 | 2 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 4 | 3 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 4 | 4 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 4 | 5 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 4 | 6 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 4 | 7 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.02928 | 100 | 1.5 | 100 | 2 | 100 | 1.9325 | 59.7846 | 0 | 0 | 0 | 0 | 0
3 | 4 | 8 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.28304 | 100 | 1.5 | 100 | 2 | 100 | 1.6788 | 51.9344 | 0 | 0 | 0 | 0 | 0
3 | 4 | 9 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.65197 | 100 | 1.5 | 100 | 2 | 100 | 1.3099 | 40.5213 | 0 | 0 | 0 | 0 | 0
3 | 4 | 10 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.99162 | 100 | 1.5 | 100 | 2 | 100 | 0.9702 | 30.014 | 0 | 0 | 0 | 0 | 0
3 | 4 | 11 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.2473 | 100 | 1.5 | 100 | 2 | 100 | 0.71449 | 22.1033 | 0 | 0 | 0 | 0 | 0
3 | 4 | 12 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.4035 | 100 | 1.5 | 100 | 2 | 100 | 0.55833 | 17.2724 | 0 | 0 | 0 | 0 | 0
3 | 4 | 13 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.4523 | 100 | 1.5 | 100 | 2 | 100 | 0.50953 | 15.7627 | 0 | 0 | 0 | 0 | 0
3 | 4 | 14 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.3801 | 100 | 1.5 | 100 | 2 | 100 | 0.58175 | 17.997 | 0 | 0 | 0 | 0 | 0
3 | 4 | 15 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.2063 | 100 | 1.5 | 100 | 2 | 100 | 0.75548 | 23.3715 | 0 | 0 | 0 | 0 | 0
3 | 4 | 16 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.93696 | 100 | 1.5 | 100 | 2 | 100 | 1.0249 | 31.7048 | 0 | 0 | 0 | 0 | 0
3 | 4 | 17 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.61293 | 100 | 1.5 | 100 | 2 | 100 | 1.3489 | 41.729 | 0 | 0 | 0 | 0 | 0
3 | 4 | 18 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.25766 | 100 | 1.5 | 100 | 2 | 100 | 1.7042 | 52.7194 | 0 | 0 | 0 | 0 | 0
3 | 4 | 19 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.01952 | 100 | 1.5 | 100 | 2 | 100 | 1.9423 | 60.0866 | 0 | 0 | 0 | 0 | 0
3 | 4 | 20 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 4 | 21 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 4 | 22 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 4 | 23 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 4 | 24 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 5 | 1 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 5 | 2 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 5 | 3 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 5 | 4 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 5 | 5 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 5 | 6 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 5 | 7 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.070272 | 100 | 1.5 | 100 | 2 | 100 | 1.8915 | 58.5165 | 0 | 0 | 0 | 0 | 0
3 | 5 | 8 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.31232 | 100 | 1.5 | 100 | 2 | 100 | 1.6495 | 51.0286 | 0 | 0 | 0 | 0 | 0
3 | 5 | 9 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.63635 | 100 | 1.5 | 100 | 2 | 100 | 1.3255 | 41.0044 | 0 | 0 | 0 | 0 | 0
3 | 5 | 10 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.94086 | 100 | 1.5 | 100 | 2 | 100 | 1.021 | 31.584 | 0 | 0 | 0 | 0 | 0
3 | 5 | 11 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.1712 | 100 | 1.5 | 100 | 2 | 100 | 0.79062 | 24.4584 | 0 | 0 | 0 | 0 | 0
3 | 5 | 12 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.3137 | 100 | 1.5 | 100 | 2 | 100 | 0.64812 | 20.0502 | 0 | 0 | 0 | 0 | 0
3 | 5 | 13 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.3527 | 100 | 1.5 | 100 | 2 | 100 | 0.60908 | 18.8425 | 0 | 0 | 0 | 0 | 0
3 | 5 | 14 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.2844 | 100 | 1.5 | 100 | 2 | 100 | 0.6774 | 20.956 | 0 | 0 | 0 | 0 | 0
3 | 5 | 15 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.1204 | 100 | 1.5 | 100 | 2 | 100 | 0.84137 | 26.0285 | 0 | 0 | 0 | 0 | 0
3 | 5 | 16 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.87254 | 100 | 1.5 | 100 | 2 | 100 | 1.0893 | 33.6976 | 0 | 0 | 0 | 0 | 0
3 | 5 | 17 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.56608 | 100 | 1.5 | 100 | 2 | 100 | 1.3957 | 43.1783 | 0 | 0 | 0 | 0 | 0
3 | 5 | 18 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.26157 | 100 | 1.5 | 100 | 2 | 100 | 1.7003 | 52.5986 | 0 | 0 | 0 | 0 | 0
3 | 5 | 19 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.037088 | 100 | 1.5 | 100 | 2 | 100 | 1.9247 | 59.5431 | 0 | 0 | 0 | 0 | 0
3 | 5 | 20 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 5 | 21 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 5 | 22 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 5 | 23 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 5 | 24 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 6 | 1 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 6 | 2 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 6 | 3 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 6 | 4 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 6 | 5 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 6 | 6 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 6 | 7 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.06832 | 100 | 1.5 | 100 | 2 | 100 | 1.8935 | 58.5769 | 0 | 0 | 0 | 0 | 0
3 | 6 | 8 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.25766 | 100 | 1.5 | 100 | 2 | 100 | 1.7042 | 52.7194 | 0 | 0 | 0 | 0 | 0
3 | 6 | 9 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.52899 | 100 | 1.5 | 100 | 2 | 100 | 1.4328 | 44.3256 | 0 | 0 | 0 | 0 | 0
3 | 6 | 10 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.80813 | 100 | 1.5 | 100 | 2 | 100 | 1.1537 | 35.6903 | 0 | 0 | 0 | 0 | 0
3 | 6 | 11 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.0287 | 100 | 1.5 | 100 | 2 | 100 | 0.93311 | 28.8666 | 0 | 0 | 0 | 0 | 0
3 | 6 | 12 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.1614 | 100 | 1.5 | 100 | 2 | 100 | 0.80038 | 24.7604 | 0 | 0 | 0 | 0 | 0
3 | 6 | 13 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.2161 | 100 | 1.5 | 100 | 2 | 100 | 0.74572 | 23.0695 | 0 | 0 | 0 | 0 | 0
3 | 6 | 14 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.1595 | 100 | 1.5 | 100 | 2 | 100 | 0.80233 | 24.8207 | 0 | 0 | 0 | 0 | 0
3 | 6 | 15 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.0111 | 100 | 1.5 | 100 | 2 | 100 | 0.95068 | 29.4101 | 0 | 0 | 0 | 0 | 0
3 | 6 | 16 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.80032 | 100 | 1.5 | 100 | 2 | 100 | 1.1615 | 35.9319 | 0 | 0 | 0 | 0 | 0
3 | 6 | 17 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.53485 | 100 | 1.5 | 100 | 2 | 100 | 1.427 | 44.1445 | 0 | 0 | 0 | 0 | 0
3 | 6 | 18 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.26352 | 100 | 1.5 | 100 | 2 | 100 | 1.6983 | 52.5382 | 0 | 0 | 0 | 0 | 0
3 | 6 | 19 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.054656 | 100 | 1.5 | 100 | 2 | 100 | 1.9072 | 58.9996 | 0 | 0 | 0 | 0 | 0
3 | 6 | 20 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 6 | 21 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 6 | 22 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 6 | 23 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 6 | 24 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 7 | 1 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 7 | 2 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 7 | 3 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 7 | 4 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 7 | 5 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 7 | 6 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 7 | 7 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.037088 | 100 | 1.5 | 100 | 2 | 100 | 1.9247 | 59.5431 | 0 | 0 | 0 | 0 | 0
3 | 7 | 8 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.1913 | 100 | 1.5 | 100 | 2 | 100 | 1.7705 | 54.7725 | 0 | 0 | 0 | 0 | 0
3 | 7 | 9 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.41578 | 100 | 1.5 | 100 | 2 | 100 | 1.546 | 47.8281 | 0 | 0 | 0 | 0 | 0
3 | 7 | 10 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.65782 | 100 | 1.5 | 100 | 2 | 100 | 1.304 | 40.3401 | 0 | 0 | 0 | 0 | 0
3 | 7 | 11 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.86083 | 100 | 1.5 | 100 | 2 | 100 | 1.101 | 34.0599 | 0 | 0 | 0 | 0 | 0
3 | 7 | 12 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.0053 | 100 | 1.5 | 100 | 2 | 100 | 0.95654 | 29.5913 | 0 | 0 | 0 | 0 | 0
3 | 7 | 13 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.058 | 100 | 1.5 | 100 | 2 | 100 | 0.90383 | 27.9608 | 0 | 0 | 0 | 0 | 0
3 | 7 | 14 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.0248 | 100 | 1.5 | 100 | 2 | 100 | 0.93702 | 28.9874 | 0 | 0 | 0 | 0 | 0
3 | 7 | 15 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.90768 | 100 | 1.5 | 100 | 2 | 100 | 1.0541 | 32.6106 | 0 | 0 | 0 | 0 | 0
3 | 7 | 16 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.70662 | 100 | 1.5 | 100 | 2 | 100 | 1.2552 | 38.8305 | 0 | 0 | 0 | 0 | 0
3 | 7 | 17 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.47434 | 100 | 1.5 | 100 | 2 | 100 | 1.4875 | 46.0165 | 0 | 0 | 0 | 0 | 0
3 | 7 | 18 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.24205 | 100 | 1.5 | 100 | 2 | 100 | 1.7198 | 53.2025 | 0 | 0 | 0 | 0 | 0
3 | 7 | 19 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.056608 | 100 | 1.5 | 100 | 2 | 100 | 1.9052 | 58.9392 | 0 | 0 | 0 | 0 | 0
3 | 7 | 20 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 7 | 21 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 7 | 22 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 7 | 23 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 7 | 24 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 8 | 1 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 8 | 2 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 8 | 3 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 8 | 4 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 8 | 5 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 8 | 6 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 8 | 7 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.021472 | 100 | 1.5 | 100 | 2 | 100 | 1.9403 | 60.0262 | 0 | 0 | 0 | 0 | 0
3 | 8 | 8 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.19715 | 100 | 1.5 | 100 | 2 | 100 | 1.7647 | 54.5914 | 0 | 0 | 0 | 0 | 0
3 | 8 | 9 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.45286 | 100 | 1.5 | 100 | 2 | 100 | 1.509 | 46.6807 | 0 | 0 | 0 | 0 | 0
3 | 8 | 10 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.71638 | 100 | 1.5 | 100 | 2 | 100 | 1.2454 | 38.5285 | 0 | 0 | 0 | 0 | 0
3 | 8 | 11 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.93696 | 100 | 1.5 | 100 | 2 | 100 | 1.0249 | 31.7048 | 0 | 0 | 0 | 0 | 0
3 | 8 | 12 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.0873 | 100 | 1.5 | 100 | 2 | 100 | 0.87455 | 27.055 | 0 | 0 | 0 | 0 | 0
3 | 8 | 13 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.1497 | 100 | 1.5 | 100 | 2 | 100 | 0.81209 | 25.1227 | 0 | 0 | 0 | 0 | 0
3 | 8 | 14 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.0951 | 100 | 1.5 | 100 | 2 | 100 | 0.86675 | 26.8135 | 0 | 0 | 0 | 0 | 0
3 | 8 | 15 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.96624 | 100 | 1.5 | 100 | 2 | 100 | 0.99558 | 30.799 | 0 | 0 | 0 | 0 | 0
3 | 8 | 16 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.74762 | 100 | 1.5 | 100 | 2 | 100 | 1.2142 | 37.5623 | 0 | 0 | 0 | 0 | 0
3 | 8 | 17 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.488 | 100 | 1.5 | 100 | 2 | 100 | 1.4738 | 45.5938 | 0 | 0 | 0 | 0 | 0
3 | 8 | 18 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.22448 | 100 | 1.5 | 100 | 2 | 100 | 1.7373 | 53.746 | 0 | 0 | 0 | 0 | 0
3 | 8 | 19 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.027328 | 100 | 1.5 | 100 | 2 | 100 | 1.9345 | 59.845 | 0 | 0 | 0 | 0 | 0
3 | 8 | 20 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 8 | 21 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 8 | 22 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 8 | 23 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 8 | 24 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 9 | 1 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 9 | 2 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 9 | 3 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 9 | 4 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 9 | 5 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 9 | 6 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 9 | 7 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.017568 | 100 | 1.5 | 100 | 2 | 100 | 1.9443 | 60.147 | 0 | 0 | 0 | 0 | 0
3 | 9 | 8 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.25376 | 100 | 1.5 | 100 | 2 | 100 | 1.7081 | 52.8402 | 0 | 0 | 0 | 0 | 0
3 | 9 | 9 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.60512 | 100 | 1.5 | 100 | 2 | 100 | 1.3567 | 41.9706 | 0 | 0 | 0 | 0 | 0
3 | 9 | 10 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.9272 | 100 | 1.5 | 100 | 2 | 100 | 1.0346 | 32.0068 | 0 | 0 | 0 | 0 | 0
3 | 9 | 11 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.1712 | 100 | 1.5 | 100 | 2 | 100 | 0.79062 | 24.4584 | 0 | 0 | 0 | 0 | 0
3 | 9 | 12 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.3235 | 100 | 1.5 | 100 | 2 | 100 | 0.63836 | 19.7483 | 0 | 0 | 0 | 0 | 0
3 | 9 | 13 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.3684 | 100 | 1.5 | 100 | 2 | 100 | 0.59347 | 18.3594 | 0 | 0 | 0 | 0 | 0
3 | 9 | 14 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.2903 | 100 | 1.5 | 100 | 2 | 100 | 0.67155 | 20.7748 | 0 | 0 | 0 | 0 | 0
3 | 9 | 15 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.099 | 100 | 1.5 | 100 | 2 | 100 | 0.86284 | 26.6927 | 0 | 0 | 0 | 0 | 0
3 | 9 | 16 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.84326 | 100 | 1.5 | 100 | 2 | 100 | 1.1186 | 34.6034 | 0 | 0 | 0 | 0 | 0
3 | 9 | 17 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.51533 | 100 | 1.5 | 100 | 2 | 100 | 1.4465 | 44.7483 | 0 | 0 | 0 | 0 | 0
3 | 9 | 18 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.16787 | 100 | 1.5 | 100 | 2 | 100 | 1.7939 | 55.4972 | 0 | 0 | 0 | 0 | 0
3 | 9 | 19 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.001952 | 100 | 1.5 | 100 | 2 | 100 | 1.9599 | 60.63 | 0 | 0 | 0 | 0 | 0
3 | 9 | 20 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 9 | 21 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 9 | 22 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 9 | 23 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 9 | 24 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 10 | 1 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 10 | 2 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 10 | 3 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 10 | 4 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 10 | 5 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 10 | 6 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 10 | 7 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 10 | 8 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.26742 | 100 | 1.5 | 100 | 2 | 100 | 1.6944 | 52.4175 | 0 | 0 | 0 | 0 | 0
3 | 10 | 9 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.71443 | 100 | 1.5 | 100 | 2 | 100 | 1.2474 | 38.5889 | 0 | 0 | 0 | 0 | 0
3 | 10 | 10 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.058 | 100 | 1.5 | 100 | 2 | 100 | 0.90383 | 27.9608 | 0 | 0 | 0 | 0 | 0
3 | 10 | 11 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.3059 | 100 | 1.5 | 100 | 2 | 100 | 0.65593 | 20.2917 | 0 | 0 | 0 | 0 | 0
3 | 10 | 12 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.4484 | 100 | 1.5 | 100 | 2 | 100 | 0.51343 | 15.8835 | 0 | 0 | 0 | 0 | 0
3 | 10 | 13 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.4718 | 100 | 1.5 | 100 | 2 | 100 | 0.49001 | 15.1589 | 0 | 0 | 0 | 0 | 0
3 | 10 | 14 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.3566 | 100 | 1.5 | 100 | 2 | 100 | 0.60518 | 18.7217 | 0 | 0 | 0 | 0 | 0
3 | 10 | 15 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.138 | 100 | 1.5 | 100 | 2 | 100 | 0.8238 | 25.485 | 0 | 0 | 0 | 0 | 0
3 | 10 | 16 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.8335 | 100 | 1.5 | 100 | 2 | 100 | 1.1283 | 34.9053 | 0 | 0 | 0 | 0 | 0
3 | 10 | 17 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.46653 | 100 | 1.5 | 100 | 2 | 100 | 1.4953 | 46.258 | 0 | 0 | 0 | 0 | 0
3 | 10 | 18 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.060512 | 100 | 1.5 | 100 | 2 | 100 | 1.9013 | 58.8184 | 0 | 0 | 0 | 0 | 0
3 | 10 | 19 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 10 | 20 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 10 | 21 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 10 | 22 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 10 | 23 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 10 | 24 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 11 | 1 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 11 | 2 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 11 | 3 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 11 | 4 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 11 | 5 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 11 | 6 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 11 | 7 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 11 | 8 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.15811 | 100 | 1.5 | 100 | 2 | 100 | 1.8037 | 55.7991 | 0 | 0 | 0 | 0 | 0
3 | 11 | 9 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.64221 | 100 | 1.5 | 100 | 2 | 100 | 1.3196 | 40.8232 | 0 | 0 | 0 | 0 | 0
3 | 11 | 10 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.0053 | 100 | 1.5 | 100 | 2 | 100 | 0.95654 | 29.5913 | 0 | 0 | 0 | 0 | 0
3 | 11 | 11 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.2571 | 100 | 1.5 | 100 | 2 | 100 | 0.70473 | 21.8014 | 0 | 0 | 0 | 0 | 0
3 | 11 | 12 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.3957 | 100 | 1.5 | 100 | 2 | 100 | 0.56614 | 17.5139 | 0 | 0 | 0 | 0 | 0
3 | 11 | 13 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.4093 | 100 | 1.5 | 100 | 2 | 100 | 0.55247 | 17.0912 | 0 | 0 | 0 | 0 | 0
3 | 11 | 14 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.3117 | 100 | 1.5 | 100 | 2 | 100 | 0.65007 | 20.1106 | 0 | 0 | 0 | 0 | 0
3 | 11 | 15 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.0931 | 100 | 1.5 | 100 | 2 | 100 | 0.8687 | 26.8739 | 0 | 0 | 0 | 0 | 0
3 | 11 | 16 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.7847 | 100 | 1.5 | 100 | 2 | 100 | 1.1771 | 36.415 | 0 | 0 | 0 | 0 | 0
3 | 11 | 17 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.3416 | 100 | 1.5 | 100 | 2 | 100 | 1.6202 | 50.1228 | 0 | 0 | 0 | 0 | 0
3 | 11 | 18 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 11 | 19 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 11 | 20 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 11 | 21 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 11 | 22 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 11 | 23 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 11 | 24 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 12 | 1 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 12 | 2 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 12 | 3 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 12 | 4 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 12 | 5 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 12 | 6 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 12 | 7 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 12 | 8 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.064416 | 100 | 1.5 | 100 | 2 | 100 | 1.8974 | 58.6977 | 0 | 0 | 0 | 0 | 0
3 | 12 | 9 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.5329 | 100 | 1.5 | 100 | 2 | 100 | 1.4289 | 44.2049 | 0 | 0 | 0 | 0 | 0
3 | 12 | 10 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.91158 | 100 | 1.5 | 100 | 2 | 100 | 1.0502 | 32.4898 | 0 | 0 | 0 | 0 | 0
3 | 12 | 11 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.1829 | 100 | 1.5 | 100 | 2 | 100 | 0.77891 | 24.0961 | 0 | 0 | 0 | 0 | 0
3 | 12 | 12 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.3488 | 100 | 1.5 | 100 | 2 | 100 | 0.61299 | 18.9632 | 0 | 0 | 0 | 0 | 0
3 | 12 | 13 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.3937 | 100 | 1.5 | 100 | 2 | 100 | 0.56809 | 17.5743 | 0 | 0 | 0 | 0 | 0
3 | 12 | 14 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.3098 | 100 | 1.5 | 100 | 2 | 100 | 0.65203 | 20.171 | 0 | 0 | 0 | 0 | 0
3 | 12 | 15 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 1.1087 | 100 | 1.5 | 100 | 2 | 100 | 0.85308 | 26.3908 | 0 | 0 | 0 | 0 | 0
3 | 12 | 16 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.81789 | 100 | 1.5 | 100 | 2 | 100 | 1.1439 | 35.3884 | 0 | 0 | 0 | 0 | 0
3 | 12 | 17 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.37674 | 100 | 1.5 | 100 | 2 | 100 | 1.5851 | 49.0358 | 0 | 0 | 0 | 0 | 0
3 | 12 | 18 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.003904 | 100 | 1.5 | 100 | 2 | 100 | 1.9579 | 60.5697 | 0 | 0 | 0 | 0 | 0
3 | 12 | 19 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 12 | 20 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 12 | 21 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 12 | 22 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 12 | 23 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
3 | 12 | 24 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9618 | 60.6904 | 0 | 0 | 0 | 0 | 0
4 | 1 | 1 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 1 | 2 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 1 | 3 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 1 | 4 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 1 | 5 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 1 | 6 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 1 | 7 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 1 | 8 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.042592 | 100 | 1.5 | 100 | 2 | 100 | 1.9283 | 60.5827 | 0 | 0 | 0 | 0 | 0
4 | 1 | 9 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.46464 | 100 | 1.5 | 100 | 2 | 100 | 1.5063 | 47.3232 | 0 | 0 | 0 | 0 | 0
4 | 1 | 10 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.85765 | 100 | 1.5 | 100 | 2 | 100 | 1.1133 | 34.9761 | 0 | 0 | 0 | 0 | 0
4 | 1 | 11 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.1539 | 100 | 1.5 | 100 | 2 | 100 | 0.81708 | 25.6702 | 0 | 0 | 0 | 0 | 0
4 | 1 | 12 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.3455 | 100 | 1.5 | 100 | 2 | 100 | 0.62542 | 19.6487 | 0 | 0 | 0 | 0 | 0
4 | 1 | 13 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.4172 | 100 | 1.5 | 100 | 2 | 100 | 0.55379 | 17.3983 | 0 | 0 | 0 | 0 | 0
4 | 1 | 14 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.3629 | 100 | 1.5 | 100 | 2 | 100 | 0.60799 | 19.1013 | 0 | 0 | 0 | 0 | 0
4 | 1 | 15 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.1945 | 100 | 1.5 | 100 | 2 | 100 | 0.77643 | 24.3929 | 0 | 0 | 0 | 0 | 0
4 | 1 | 16 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.91186 | 100 | 1.5 | 100 | 2 | 100 | 1.0591 | 33.2731 | 0 | 0 | 0 | 0 | 0
4 | 1 | 17 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.54982 | 100 | 1.5 | 100 | 2 | 100 | 1.4211 | 44.647 | 0 | 0 | 0 | 0 | 0
4 | 1 | 18 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.07744 | 100 | 1.5 | 100 | 2 | 100 | 1.8935 | 59.4879 | 0 | 0 | 0 | 0 | 0
4 | 1 | 19 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 1 | 20 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 1 | 21 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 1 | 22 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 1 | 23 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 1 | 24 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 2 | 1 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 2 | 2 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 2 | 3 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 2 | 4 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 2 | 5 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 2 | 6 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 2 | 7 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 2 | 8 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.069696 | 100 | 1.5 | 100 | 2 | 100 | 1.9012 | 59.7312 | 0 | 0 | 0 | 0 | 0
4 | 2 | 9 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.50723 | 100 | 1.5 | 100 | 2 | 100 | 1.4637 | 45.9851 | 0 | 0 | 0 | 0 | 0
4 | 2 | 10 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.90024 | 100 | 1.5 | 100 | 2 | 100 | 1.0707 | 33.638 | 0 | 0 | 0 | 0 | 0
4 | 2 | 11 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.2081 | 100 | 1.5 | 100 | 2 | 100 | 0.76287 | 23.9672 | 0 | 0 | 0 | 0 | 0
4 | 2 | 12 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.4152 | 100 | 1.5 | 100 | 2 | 100 | 0.55572 | 17.4591 | 0 | 0 | 0 | 0 | 0
4 | 2 | 13 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.4965 | 100 | 1.5 | 100 | 2 | 100 | 0.47441 | 14.9045 | 0 | 0 | 0 | 0 | 0
4 | 2 | 14 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.4578 | 100 | 1.5 | 100 | 2 | 100 | 0.51313 | 16.121 | 0 | 0 | 0 | 0 | 0
4 | 2 | 15 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.2971 | 100 | 1.5 | 100 | 2 | 100 | 0.67382 | 21.1693 | 0 | 0 | 0 | 0 | 0
4 | 2 | 16 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.03 | 100 | 1.5 | 100 | 2 | 100 | 0.94099 | 29.5629 | 0 | 0 | 0 | 0 | 0
4 | 2 | 17 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.67179 | 100 | 1.5 | 100 | 2 | 100 | 1.2991 | 40.8152 | 0 | 0 | 0 | 0 | 0
4 | 2 | 18 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.17618 | 100 | 1.5 | 100 | 2 | 100 | 1.7948 | 56.3859 | 0 | 0 | 0 | 0 | 0
4 | 2 | 19 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 2 | 20 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 2 | 21 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 2 | 22 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 2 | 23 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 2 | 24 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 3 | 1 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 3 | 2 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 3 | 3 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 3 | 4 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 3 | 5 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 3 | 6 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 3 | 7 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.001936 | 100 | 1.5 | 100 | 2 | 100 | 1.969 | 61.86 | 0 | 0 | 0 | 0 | 0
4 | 3 | 8 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.16069 | 100 | 1.5 | 100 | 2 | 100 | 1.8103 | 56.8725 | 0 | 0 | 0 | 0 | 0
4 | 3 | 9 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.58274 | 100 | 1.5 | 100 | 2 | 100 | 1.3882 | 43.613 | 0 | 0 | 0 | 0 | 0
4 | 3 | 10 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.96026 | 100 | 1.5 | 100 | 2 | 100 | 1.0107 | 31.7525 | 0 | 0 | 0 | 0 | 0
4 | 3 | 11 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.2429 | 100 | 1.5 | 100 | 2 | 100 | 0.72803 | 22.8723 | 0 | 0 | 0 | 0 | 0
4 | 3 | 12 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.4384 | 100 | 1.5 | 100 | 2 | 100 | 0.53249 | 16.7292 | 0 | 0 | 0 | 0 | 0
4 | 3 | 13 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.512 | 100 | 1.5 | 100 | 2 | 100 | 0.45892 | 14.4179 | 0 | 0 | 0 | 0 | 0
4 | 3 | 14 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.4772 | 100 | 1.5 | 100 | 2 | 100 | 0.49377 | 15.5127 | 0 | 0 | 0 | 0 | 0
4 | 3 | 15 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.2797 | 100 | 1.5 | 100 | 2 | 100 | 0.69124 | 21.7167 | 0 | 0 | 0 | 0 | 0
4 | 3 | 16 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.0145 | 100 | 1.5 | 100 | 2 | 100 | 0.95647 | 30.0495 | 0 | 0 | 0 | 0 | 0
4 | 3 | 17 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.66405 | 100 | 1.5 | 100 | 2 | 100 | 1.3069 | 41.0585 | 0 | 0 | 0 | 0 | 0
4 | 3 | 18 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.24974 | 100 | 1.5 | 100 | 2 | 100 | 1.7212 | 54.0746 | 0 | 0 | 0 | 0 | 0
4 | 3 | 19 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.001936 | 100 | 1.5 | 100 | 2 | 100 | 1.969 | 61.86 | 0 | 0 | 0 | 0 | 0
4 | 3 | 20 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 3 | 21 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 3 | 22 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 3 | 23 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 3 | 24 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 4 | 1 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 4 | 2 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 4 | 3 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 4 | 4 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 4 | 5 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 4 | 6 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 4 | 7 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.02904 | 100 | 1.5 | 100 | 2 | 100 | 1.9419 | 61.0084 | 0 | 0 | 0 | 0 | 0
4 | 4 | 8 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.28072 | 100 | 1.5 | 100 | 2 | 100 | 1.6902 | 53.1014 | 0 | 0 | 0 | 0 | 0
4 | 4 | 9 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.64662 | 100 | 1.5 | 100 | 2 | 100 | 1.3243 | 41.6059 | 0 | 0 | 0 | 0 | 0
4 | 4 | 10 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.98349 | 100 | 1.5 | 100 | 2 | 100 | 0.98745 | 31.0226 | 0 | 0 | 0 | 0 | 0
4 | 4 | 11 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.2371 | 100 | 1.5 | 100 | 2 | 100 | 0.73383 | 23.0548 | 0 | 0 | 0 | 0 | 0
4 | 4 | 12 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.392 | 100 | 1.5 | 100 | 2 | 100 | 0.57895 | 18.189 | 0 | 0 | 0 | 0 | 0
4 | 4 | 13 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.4404 | 100 | 1.5 | 100 | 2 | 100 | 0.53055 | 16.6684 | 0 | 0 | 0 | 0 | 0
4 | 4 | 14 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.3688 | 100 | 1.5 | 100 | 2 | 100 | 0.60219 | 18.9188 | 0 | 0 | 0 | 0 | 0
4 | 4 | 15 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.1964 | 100 | 1.5 | 100 | 2 | 100 | 0.77449 | 24.3321 | 0 | 0 | 0 | 0 | 0
4 | 4 | 16 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.92928 | 100 | 1.5 | 100 | 2 | 100 | 1.0417 | 32.7257 | 0 | 0 | 0 | 0 | 0
4 | 4 | 17 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.6079 | 100 | 1.5 | 100 | 2 | 100 | 1.363 | 42.8223 | 0 | 0 | 0 | 0 | 0
4 | 4 | 18 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.25555 | 100 | 1.5 | 100 | 2 | 100 | 1.7154 | 53.8921 | 0 | 0 | 0 | 0 | 0
4 | 4 | 19 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.01936 | 100 | 1.5 | 100 | 2 | 100 | 1.9516 | 61.3126 | 0 | 0 | 0 | 0 | 0
4 | 4 | 20 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 4 | 21 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 4 | 22 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 4 | 23 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 4 | 24 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 5 | 1 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 5 | 2 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 5 | 3 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 5 | 4 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 5 | 5 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 5 | 6 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 5 | 7 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.069696 | 100 | 1.5 | 100 | 2 | 100 | 1.9012 | 59.7312 | 0 | 0 | 0 | 0 | 0
4 | 5 | 8 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.30976 | 100 | 1.5 | 100 | 2 | 100 | 1.6612 | 52.1891 | 0 | 0 | 0 | 0 | 0
4 | 5 | 9 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.63114 | 100 | 1.5 | 100 | 2 | 100 | 1.3398 | 42.0924 | 0 | 0 | 0 | 0 | 0
4 | 5 | 10 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.93315 | 100 | 1.5 | 100 | 2 | 100 | 1.0378 | 32.604 | 0 | 0 | 0 | 0 | 0
4 | 5 | 11 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.1616 | 100 | 1.5 | 100 | 2 | 100 | 0.80934 | 25.4269 | 0 | 0 | 0 | 0 | 0
4 | 5 | 12 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.3029 | 100 | 1.5 | 100 | 2 | 100 | 0.66801 | 20.9868 | 0 | 0 | 0 | 0 | 0
4 | 5 | 13 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.3416 | 100 | 1.5 | 100 | 2 | 100 | 0.62929 | 19.7704 | 0 | 0 | 0 | 0 | 0
4 | 5 | 14 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.2739 | 100 | 1.5 | 100 | 2 | 100 | 0.69705 | 21.8992 | 0 | 0 | 0 | 0 | 0
4 | 5 | 15 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.1113 | 100 | 1.5 | 100 | 2 | 100 | 0.85967 | 27.0083 | 0 | 0 | 0 | 0 | 0
4 | 5 | 16 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.86539 | 100 | 1.5 | 100 | 2 | 100 | 1.1055 | 34.7329 | 0 | 0 | 0 | 0 | 0
4 | 5 | 17 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.56144 | 100 | 1.5 | 100 | 2 | 100 | 1.4095 | 44.2821 | 0 | 0 | 0 | 0 | 0
4 | 5 | 18 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.25942 | 100 | 1.5 | 100 | 2 | 100 | 1.7115 | 53.7705 | 0 | 0 | 0 | 0 | 0
4 | 5 | 19 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.036784 | 100 | 1.5 | 100 | 2 | 100 | 1.9342 | 60.7651 | 0 | 0 | 0 | 0 | 0
4 | 5 | 20 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 5 | 21 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 5 | 22 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 5 | 23 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 5 | 24 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 6 | 1 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 6 | 2 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 6 | 3 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 6 | 4 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 6 | 5 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 6 | 6 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 6 | 7 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.06776 | 100 | 1.5 | 100 | 2 | 100 | 1.9032 | 59.792 | 0 | 0 | 0 | 0 | 0
4 | 6 | 8 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.25555 | 100 | 1.5 | 100 | 2 | 100 | 1.7154 | 53.8921 | 0 | 0 | 0 | 0 | 0
4 | 6 | 9 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.52466 | 100 | 1.5 | 100 | 2 | 100 | 1.4463 | 45.4377 | 0 | 0 | 0 | 0 | 0
4 | 6 | 10 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.8015 | 100 | 1.5 | 100 | 2 | 100 | 1.1694 | 36.74 | 0 | 0 | 0 | 0 | 0
4 | 6 | 11 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.0203 | 100 | 1.5 | 100 | 2 | 100 | 0.95067 | 29.867 | 0 | 0 | 0 | 0 | 0
4 | 6 | 12 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.1519 | 100 | 1.5 | 100 | 2 | 100 | 0.81902 | 25.731 | 0 | 0 | 0 | 0 | 0
4 | 6 | 13 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.2061 | 100 | 1.5 | 100 | 2 | 100 | 0.76481 | 24.028 | 0 | 0 | 0 | 0 | 0
4 | 6 | 14 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.15 | 100 | 1.5 | 100 | 2 | 100 | 0.82095 | 25.7919 | 0 | 0 | 0 | 0 | 0
4 | 6 | 15 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.0028 | 100 | 1.5 | 100 | 2 | 100 | 0.96809 | 30.4144 | 0 | 0 | 0 | 0 | 0
4 | 6 | 16 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.79376 | 100 | 1.5 | 100 | 2 | 100 | 1.1772 | 36.9833 | 0 | 0 | 0 | 0 | 0
4 | 6 | 17 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.53046 | 100 | 1.5 | 100 | 2 | 100 | 1.4405 | 45.2553 | 0 | 0 | 0 | 0 | 0
4 | 6 | 18 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.26136 | 100 | 1.5 | 100 | 2 | 100 | 1.7096 | 53.7097 | 0 | 0 | 0 | 0 | 0
4 | 6 | 19 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.054208 | 100 | 1.5 | 100 | 2 | 100 | 1.9167 | 60.2177 | 0 | 0 | 0 | 0 | 0
4 | 6 | 20 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 6 | 21 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 6 | 22 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 6 | 23 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 6 | 24 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 7 | 1 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 7 | 2 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 7 | 3 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 7 | 4 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 7 | 5 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 7 | 6 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 7 | 7 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.036784 | 100 | 1.5 | 100 | 2 | 100 | 1.9342 | 60.7651 | 0 | 0 | 0 | 0 | 0
4 | 7 | 8 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.18973 | 100 | 1.5 | 100 | 2 | 100 | 1.7812 | 55.9601 | 0 | 0 | 0 | 0 | 0
4 | 7 | 9 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.41237 | 100 | 1.5 | 100 | 2 | 100 | 1.5586 | 48.9655 | 0 | 0 | 0 | 0 | 0
4 | 7 | 10 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.65243 | 100 | 1.5 | 100 | 2 | 100 | 1.3185 | 41.4234 | 0 | 0 | 0 | 0 | 0
4 | 7 | 11 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.85378 | 100 | 1.5 | 100 | 2 | 100 | 1.1172 | 35.0978 | 0 | 0 | 0 | 0 | 0
4 | 7 | 12 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.99704 | 100 | 1.5 | 100 | 2 | 100 | 0.9739 | 30.5969 | 0 | 0 | 0 | 0 | 0
4 | 7 | 13 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.0493 | 100 | 1.5 | 100 | 2 | 100 | 0.92163 | 28.9547 | 0 | 0 | 0 | 0 | 0
4 | 7 | 14 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.0164 | 100 | 1.5 | 100 | 2 | 100 | 0.95454 | 29.9886 | 0 | 0 | 0 | 0 | 0
4 | 7 | 15 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.90024 | 100 | 1.5 | 100 | 2 | 100 | 1.0707 | 33.638 | 0 | 0 | 0 | 0 | 0
4 | 7 | 16 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.70083 | 100 | 1.5 | 100 | 2 | 100 | 1.2701 | 39.9028 | 0 | 0 | 0 | 0 | 0
4 | 7 | 17 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.47045 | 100 | 1.5 | 100 | 2 | 100 | 1.5005 | 47.1408 | 0 | 0 | 0 | 0 | 0
4 | 7 | 18 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.24006 | 100 | 1.5 | 100 | 2 | 100 | 1.7309 | 54.3787 | 0 | 0 | 0 | 0 | 0
4 | 7 | 19 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.056144 | 100 | 1.5 | 100 | 2 | 100 | 1.9148 | 60.1569 | 0 | 0 | 0 | 0 | 0
4 | 7 | 20 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 7 | 21 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 7 | 22 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 7 | 23 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 7 | 24 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 8 | 1 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 8 | 2 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 8 | 3 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 8 | 4 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 8 | 5 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 8 | 6 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 8 | 7 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.021296 | 100 | 1.5 | 100 | 2 | 100 | 1.9496 | 61.2517 | 0 | 0 | 0 | 0 | 0
4 | 8 | 8 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.19554 | 100 | 1.5 | 100 | 2 | 100 | 1.7754 | 55.7777 | 0 | 0 | 0 | 0 | 0
4 | 8 | 9 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.44915 | 100 | 1.5 | 100 | 2 | 100 | 1.5218 | 47.8098 | 0 | 0 | 0 | 0 | 0
4 | 8 | 10 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.71051 | 100 | 1.5 | 100 | 2 | 100 | 1.2604 | 39.5987 | 0 | 0 | 0 | 0 | 0
4 | 8 | 11 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.92928 | 100 | 1.5 | 100 | 2 | 100 | 1.0417 | 32.7257 | 0 | 0 | 0 | 0 | 0
4 | 8 | 12 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.0784 | 100 | 1.5 | 100 | 2 | 100 | 0.89259 | 28.0423 | 0 | 0 | 0 | 0 | 0
4 | 8 | 13 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.1403 | 100 | 1.5 | 100 | 2 | 100 | 0.83063 | 26.096 | 0 | 0 | 0 | 0 | 0
4 | 8 | 14 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.0861 | 100 | 1.5 | 100 | 2 | 100 | 0.88484 | 27.799 | 0 | 0 | 0 | 0 | 0
4 | 8 | 15 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.95832 | 100 | 1.5 | 100 | 2 | 100 | 1.0126 | 31.8133 | 0 | 0 | 0 | 0 | 0
4 | 8 | 16 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.74149 | 100 | 1.5 | 100 | 2 | 100 | 1.2295 | 38.6255 | 0 | 0 | 0 | 0 | 0
4 | 8 | 17 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.484 | 100 | 1.5 | 100 | 2 | 100 | 1.4869 | 46.715 | 0 | 0 | 0 | 0 | 0
4 | 8 | 18 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.22264 | 100 | 1.5 | 100 | 2 | 100 | 1.7483 | 54.9261 | 0 | 0 | 0 | 0 | 0
4 | 8 | 19 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.027104 | 100 | 1.5 | 100 | 2 | 100 | 1.9438 | 61.0693 | 0 | 0 | 0 | 0 | 0
4 | 8 | 20 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 8 | 21 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 8 | 22 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 8 | 23 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 8 | 24 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 9 | 1 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 9 | 2 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 9 | 3 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 9 | 4 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 9 | 5 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 9 | 6 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 9 | 7 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.017424 | 100 | 1.5 | 100 | 2 | 100 | 1.9535 | 61.3734 | 0 | 0 | 0 | 0 | 0
4 | 9 | 8 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.25168 | 100 | 1.5 | 100 | 2 | 100 | 1.7193 | 54.0138 | 0 | 0 | 0 | 0 | 0
4 | 9 | 9 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.60016 | 100 | 1.5 | 100 | 2 | 100 | 1.3708 | 43.0656 | 0 | 0 | 0 | 0 | 0
4 | 9 | 10 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.9196 | 100 | 1.5 | 100 | 2 | 100 | 1.0513 | 33.0298 | 0 | 0 | 0 | 0 | 0
4 | 9 | 11 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.1616 | 100 | 1.5 | 100 | 2 | 100 | 0.80934 | 25.4269 | 0 | 0 | 0 | 0 | 0
4 | 9 | 12 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.3126 | 100 | 1.5 | 100 | 2 | 100 | 0.65833 | 20.6827 | 0 | 0 | 0 | 0 | 0
4 | 9 | 13 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.3571 | 100 | 1.5 | 100 | 2 | 100 | 0.6138 | 19.2838 | 0 | 0 | 0 | 0 | 0
4 | 9 | 14 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.2797 | 100 | 1.5 | 100 | 2 | 100 | 0.69124 | 21.7167 | 0 | 0 | 0 | 0 | 0
4 | 9 | 15 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.09 | 100 | 1.5 | 100 | 2 | 100 | 0.88097 | 27.6774 | 0 | 0 | 0 | 0 | 0
4 | 9 | 16 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.83635 | 100 | 1.5 | 100 | 2 | 100 | 1.1346 | 35.6452 | 0 | 0 | 0 | 0 | 0
4 | 9 | 17 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.5111 | 100 | 1.5 | 100 | 2 | 100 | 1.4598 | 45.8635 | 0 | 0 | 0 | 0 | 0
4 | 9 | 18 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.1665 | 100 | 1.5 | 100 | 2 | 100 | 1.8044 | 56.69 | 0 | 0 | 0 | 0 | 0
4 | 9 | 19 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.001936 | 100 | 1.5 | 100 | 2 | 100 | 1.969 | 61.86 | 0 | 0 | 0 | 0 | 0
4 | 9 | 20 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 9 | 21 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 9 | 22 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 9 | 23 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 9 | 24 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 10 | 1 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 10 | 2 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 10 | 3 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 10 | 4 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 10 | 5 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 10 | 6 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 10 | 7 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 10 | 8 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.26523 | 100 | 1.5 | 100 | 2 | 100 | 1.7057 | 53.588 | 0 | 0 | 0 | 0 | 0
4 | 10 | 9 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.70858 | 100 | 1.5 | 100 | 2 | 100 | 1.2624 | 39.6595 | 0 | 0 | 0 | 0 | 0
4 | 10 | 10 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.0493 | 100 | 1.5 | 100 | 2 | 100 | 0.92163 | 28.9547 | 0 | 0 | 0 | 0 | 0
4 | 10 | 11 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.2952 | 100 | 1.5 | 100 | 2 | 100 | 0.67575 | 21.2301 | 0 | 0 | 0 | 0 | 0
4 | 10 | 12 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.4365 | 100 | 1.5 | 100 | 2 | 100 | 0.53443 | 16.79 | 0 | 0 | 0 | 0 | 0
4 | 10 | 13 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.4597 | 100 | 1.5 | 100 | 2 | 100 | 0.51119 | 16.0602 | 0 | 0 | 0 | 0 | 0
4 | 10 | 14 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.3455 | 100 | 1.5 | 100 | 2 | 100 | 0.62542 | 19.6487 | 0 | 0 | 0 | 0 | 0
4 | 10 | 15 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.1287 | 100 | 1.5 | 100 | 2 | 100 | 0.84225 | 26.4609 | 0 | 0 | 0 | 0 | 0
4 | 10 | 16 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.82667 | 100 | 1.5 | 100 | 2 | 100 | 1.1443 | 35.9493 | 0 | 0 | 0 | 0 | 0
4 | 10 | 17 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.4627 | 100 | 1.5 | 100 | 2 | 100 | 1.5082 | 47.3841 | 0 | 0 | 0 | 0 | 0
4 | 10 | 18 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.060016 | 100 | 1.5 | 100 | 2 | 100 | 1.9109 | 60.0353 | 0 | 0 | 0 | 0 | 0
4 | 10 | 19 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 10 | 20 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 10 | 21 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 10 | 22 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 10 | 23 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 10 | 24 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 11 | 1 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 11 | 2 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 11 | 3 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 11 | 4 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 11 | 5 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 11 | 6 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 11 | 7 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 11 | 8 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.15682 | 100 | 1.5 | 100 | 2 | 100 | 1.8141 | 56.9941 | 0 | 0 | 0 | 0 | 0
4 | 11 | 9 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.63694 | 100 | 1.5 | 100 | 2 | 100 | 1.334 | 41.91 | 0 | 0 | 0 | 0 | 0
4 | 11 | 10 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.99704 | 100 | 1.5 | 100 | 2 | 100 | 0.9739 | 30.5969 | 0 | 0 | 0 | 0 | 0
4 | 11 | 11 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.2468 | 100 | 1.5 | 100 | 2 | 100 | 0.72415 | 22.7507 | 0 | 0 | 0 | 0 | 0
4 | 11 | 12 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.3842 | 100 | 1.5 | 100 | 2 | 100 | 0.5867 | 18.4323 | 0 | 0 | 0 | 0 | 0
4 | 11 | 13 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.3978 | 100 | 1.5 | 100 | 2 | 100 | 0.57315 | 18.0065 | 0 | 0 | 0 | 0 | 0
4 | 11 | 14 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.301 | 100 | 1.5 | 100 | 2 | 100 | 0.66995 | 21.0476 | 0 | 0 | 0 | 0 | 0
4 | 11 | 15 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.0842 | 100 | 1.5 | 100 | 2 | 100 | 0.88678 | 27.8598 | 0 | 0 | 0 | 0 | 0
4 | 11 | 16 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.77827 | 100 | 1.5 | 100 | 2 | 100 | 1.1927 | 37.4699 | 0 | 0 | 0 | 0 | 0
4 | 11 | 17 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.3388 | 100 | 1.5 | 100 | 2 | 100 | 1.6321 | 51.2767 | 0 | 0 | 0 | 0 | 0
4 | 11 | 18 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 11 | 19 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 11 | 20 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 11 | 21 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 11 | 22 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 11 | 23 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 11 | 24 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 12 | 1 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 12 | 2 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 12 | 3 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 12 | 4 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 12 | 5 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 12 | 6 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 12 | 7 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 12 | 8 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.063888 | 100 | 1.5 | 100 | 2 | 100 | 1.9071 | 59.9136 | 0 | 0 | 0 | 0 | 0
4 | 12 | 9 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.52853 | 100 | 1.5 | 100 | 2 | 100 | 1.4424 | 45.3161 | 0 | 0 | 0 | 0 | 0
4 | 12 | 10 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.90411 | 100 | 1.5 | 100 | 2 | 100 | 1.0668 | 33.5164 | 0 | 0 | 0 | 0 | 0
4 | 12 | 11 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.1732 | 100 | 1.5 | 100 | 2 | 100 | 0.79772 | 25.062 | 0 | 0 | 0 | 0 | 0
4 | 12 | 12 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.3378 | 100 | 1.5 | 100 | 2 | 100 | 0.63316 | 19.892 | 0 | 0 | 0 | 0 | 0
4 | 12 | 13 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.3823 | 100 | 1.5 | 100 | 2 | 100 | 0.58863 | 18.4931 | 0 | 0 | 0 | 0 | 0
4 | 12 | 14 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.2991 | 100 | 1.5 | 100 | 2 | 100 | 0.67188 | 21.1085 | 0 | 0 | 0 | 0 | 0
4 | 12 | 15 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 1.0996 | 100 | 1.5 | 100 | 2 | 100 | 0.87129 | 27.3733 | 0 | 0 | 0 | 0 | 0
4 | 12 | 16 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.81118 | 100 | 1.5 | 100 | 2 | 100 | 1.1598 | 36.4359 | 0 | 0 | 0 | 0 | 0
4 | 12 | 17 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.37365 | 100 | 1.5 | 100 | 2 | 100 | 1.5973 | 50.1819 | 0 | 0 | 0 | 0 | 0
4 | 12 | 18 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.003872 | 100 | 1.5 | 100 | 2 | 100 | 1.9671 | 61.7991 | 0 | 0 | 0 | 0 | 0
4 | 12 | 19 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 12 | 20 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 12 | 21 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 12 | 22 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 12 | 23 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
4 | 12 | 24 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0 | 0 | 1.5 | 100 | 2 | 100 | 1.9709 | 61.9208 | 0 | 0 | 0 | 0 | 0
5 | 1 | 1 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 1 | 2 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 1 | 3 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 1 | 4 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 1 | 5 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 1 | 6 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 1 | 7 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 1 | 8 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.04224 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.80432 | 17.8738 | 0 | 0 | 0
5 | 1 | 9 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.4608 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.38576 | 8.5724 | 0 | 0 | 0
5 | 1 | 10 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.85056 | 100 | 1.5 | 100 | 2 | 100 | 3.1295 | 99.8723 | 0 | 0 | 0 | 0 | 0
5 | 1 | 11 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.1443 | 100 | 1.5 | 100 | 2 | 100 | 2.8357 | 90.4975 | 0 | 0 | 0 | 0 | 0
5 | 1 | 12 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.3344 | 100 | 1.5 | 100 | 2 | 100 | 2.6457 | 84.4314 | 0 | 0 | 0 | 0 | 0
5 | 1 | 13 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.4054 | 100 | 1.5 | 100 | 2 | 100 | 2.5746 | 82.1643 | 0 | 0 | 0 | 0 | 0
5 | 1 | 14 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.3517 | 100 | 1.5 | 100 | 2 | 100 | 2.6284 | 83.88 | 0 | 0 | 0 | 0 | 0
5 | 1 | 15 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.1846 | 100 | 1.5 | 100 | 2 | 100 | 2.7954 | 89.2108 | 0 | 0 | 0 | 0 | 0
5 | 1 | 16 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.90432 | 100 | 1.5 | 100 | 2 | 100 | 3.0757 | 98.1567 | 0 | 0 | 0 | 0 | 0
5 | 1 | 17 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.54528 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.30128 | 6.6951 | 0 | 0 | 0
5 | 1 | 18 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.0768 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.76976 | 17.1058 | 0 | 0 | 0
5 | 1 | 19 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 1 | 20 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 1 | 21 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 1 | 22 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 1 | 23 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 1 | 24 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 2 | 1 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 2 | 2 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 2 | 3 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 2 | 4 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 2 | 5 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 2 | 6 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 2 | 7 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 2 | 8 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.06912 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.77744 | 17.2764 | 0 | 0 | 0
5 | 2 | 9 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.50304 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.34352 | 7.6338 | 0 | 0 | 0
5 | 2 | 10 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.8928 | 100 | 1.5 | 100 | 2 | 100 | 3.0873 | 98.5243 | 0 | 0 | 0 | 0 | 0
5 | 2 | 11 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.1981 | 100 | 1.5 | 100 | 2 | 100 | 2.782 | 88.7818 | 0 | 0 | 0 | 0 | 0
5 | 2 | 12 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.4035 | 100 | 1.5 | 100 | 2 | 100 | 2.5765 | 82.2256 | 0 | 0 | 0 | 0 | 0
5 | 2 | 13 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.4842 | 100 | 1.5 | 100 | 2 | 100 | 2.4959 | 79.6521 | 0 | 0 | 0 | 0 | 0
5 | 2 | 14 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.4458 | 100 | 1.5 | 100 | 2 | 100 | 2.5343 | 80.8776 | 0 | 0 | 0 | 0 | 0
5 | 2 | 15 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.2864 | 100 | 1.5 | 100 | 2 | 100 | 2.6937 | 85.9633 | 0 | 0 | 0 | 0 | 0
5 | 2 | 16 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.0214 | 100 | 1.5 | 100 | 2 | 100 | 2.9586 | 94.419 | 0 | 0 | 0 | 0 | 0
5 | 2 | 17 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.66624 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.18032 | 4.0071 | 0 | 0 | 0
5 | 2 | 18 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.17472 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.67184 | 14.9298 | 0 | 0 | 0
5 | 2 | 19 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 2 | 20 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 2 | 21 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 2 | 22 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 2 | 23 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 2 | 24 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 3 | 1 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 3 | 2 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 3 | 3 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 3 | 4 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 3 | 5 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 3 | 6 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 3 | 7 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.00192 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84464 | 18.7698 | 0 | 0 | 0
5 | 3 | 8 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.15936 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.6872 | 15.2711 | 0 | 0 | 0
5 | 3 | 9 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.57792 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.26864 | 5.9698 | 0 | 0 | 0
5 | 3 | 10 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.95232 | 100 | 1.5 | 100 | 2 | 100 | 3.0277 | 96.6248 | 0 | 0 | 0 | 0 | 0
5 | 3 | 11 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.2326 | 100 | 1.5 | 100 | 2 | 100 | 2.7474 | 87.6789 | 0 | 0 | 0 | 0 | 0
5 | 3 | 12 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.4266 | 100 | 1.5 | 100 | 2 | 100 | 2.5535 | 81.4903 | 0 | 0 | 0 | 0 | 0
5 | 3 | 13 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.4995 | 100 | 1.5 | 100 | 2 | 100 | 2.4805 | 79.1619 | 0 | 0 | 0 | 0 | 0
5 | 3 | 14 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.465 | 100 | 1.5 | 100 | 2 | 100 | 2.5151 | 80.2648 | 0 | 0 | 0 | 0 | 0
5 | 3 | 15 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.2691 | 100 | 1.5 | 100 | 2 | 100 | 2.7109 | 86.5147 | 0 | 0 | 0 | 0 | 0
5 | 3 | 16 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.0061 | 100 | 1.5 | 100 | 2 | 100 | 2.974 | 94.9092 | 0 | 0 | 0 | 0 | 0
5 | 3 | 17 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.65856 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.188 | 4.1778 | 0 | 0 | 0
5 | 3 | 18 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.24768 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.59888 | 13.3084 | 0 | 0 | 0
5 | 3 | 19 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.00192 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84464 | 18.7698 | 0 | 0 | 0
5 | 3 | 20 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 3 | 21 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 3 | 22 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 3 | 23 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 3 | 24 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 4 | 1 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 4 | 2 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 4 | 3 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 4 | 4 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 4 | 5 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 4 | 6 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 4 | 7 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.0288 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.81776 | 18.1724 | 0 | 0 | 0
5 | 4 | 8 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.2784 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.56816 | 12.6258 | 0 | 0 | 0
5 | 4 | 9 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.64128 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.20528 | 4.5618 | 0 | 0 | 0
5 | 4 | 10 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.97536 | 100 | 1.5 | 100 | 2 | 100 | 3.0047 | 95.8895 | 0 | 0 | 0 | 0 | 0
5 | 4 | 11 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.2269 | 100 | 1.5 | 100 | 2 | 100 | 2.7532 | 87.8627 | 0 | 0 | 0 | 0 | 0
5 | 4 | 12 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.3805 | 100 | 1.5 | 100 | 2 | 100 | 2.5996 | 82.9609 | 0 | 0 | 0 | 0 | 0
5 | 4 | 13 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.4285 | 100 | 1.5 | 100 | 2 | 100 | 2.5516 | 81.429 | 0 | 0 | 0 | 0 | 0
5 | 4 | 14 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.3574 | 100 | 1.5 | 100 | 2 | 100 | 2.6226 | 83.6962 | 0 | 0 | 0 | 0 | 0
5 | 4 | 15 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.1866 | 100 | 1.5 | 100 | 2 | 100 | 2.7935 | 89.1495 | 0 | 0 | 0 | 0 | 0
5 | 4 | 16 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.9216 | 100 | 1.5 | 100 | 2 | 100 | 3.0585 | 97.6052 | 0 | 0 | 0 | 0 | 0
5 | 4 | 17 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.60288 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.24368 | 5.4151 | 0 | 0 | 0
5 | 4 | 18 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.25344 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.59312 | 13.1804 | 0 | 0 | 0
5 | 4 | 19 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.0192 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.82736 | 18.3858 | 0 | 0 | 0
5 | 4 | 20 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 4 | 21 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 4 | 22 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 4 | 23 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 4 | 24 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 5 | 1 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 5 | 2 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 5 | 3 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 5 | 4 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 5 | 5 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 5 | 6 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 5 | 7 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.06912 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.77744 | 17.2764 | 0 | 0 | 0
5 | 5 | 8 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.3072 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.53936 | 11.9858 | 0 | 0 | 0
5 | 5 | 9 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.62592 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.22064 | 4.9031 | 0 | 0 | 0
5 | 5 | 10 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.92544 | 100 | 1.5 | 100 | 2 | 100 | 3.0546 | 97.4827 | 0 | 0 | 0 | 0 | 0
5 | 5 | 11 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.152 | 100 | 1.5 | 100 | 2 | 100 | 2.8281 | 90.2524 | 0 | 0 | 0 | 0 | 0
5 | 5 | 12 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.2922 | 100 | 1.5 | 100 | 2 | 100 | 2.6879 | 85.7794 | 0 | 0 | 0 | 0 | 0
5 | 5 | 13 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.3306 | 100 | 1.5 | 100 | 2 | 100 | 2.6495 | 84.554 | 0 | 0 | 0 | 0 | 0
5 | 5 | 14 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.2634 | 100 | 1.5 | 100 | 2 | 100 | 2.7167 | 86.6985 | 0 | 0 | 0 | 0 | 0
5 | 5 | 15 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.1021 | 100 | 1.5 | 100 | 2 | 100 | 2.878 | 91.8455 | 0 | 0 | 0 | 0 | 0
5 | 5 | 16 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.85824 | 100 | 1.5 | 100 | 2 | 100 | 3.1218 | 99.6272 | 0 | 0 | 0 | 0 | 0
5 | 5 | 17 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.5568 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.28976 | 6.4391 | 0 | 0 | 0
5 | 5 | 18 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.25728 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.58928 | 13.0951 | 0 | 0 | 0
5 | 5 | 19 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.03648 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.81008 | 18.0018 | 0 | 0 | 0
5 | 5 | 20 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 5 | 21 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 5 | 22 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 5 | 23 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 5 | 24 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 6 | 1 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 6 | 2 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 6 | 3 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 6 | 4 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 6 | 5 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 6 | 6 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 6 | 7 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.0672 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.77936 | 17.3191 | 0 | 0 | 0
5 | 6 | 8 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.25344 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.59312 | 13.1804 | 0 | 0 | 0
5 | 6 | 9 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.52032 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.32624 | 7.2498 | 0 | 0 | 0
5 | 6 | 10 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.79488 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.051679 | 1.1484 | 0 | 0 | 0
5 | 6 | 11 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.0118 | 100 | 1.5 | 100 | 2 | 100 | 2.9682 | 94.7254 | 0 | 0 | 0 | 0 | 0
5 | 6 | 12 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.1424 | 100 | 1.5 | 100 | 2 | 100 | 2.8377 | 90.5588 | 0 | 0 | 0 | 0 | 0
5 | 6 | 13 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.1962 | 100 | 1.5 | 100 | 2 | 100 | 2.7839 | 88.8431 | 0 | 0 | 0 | 0 | 0
5 | 6 | 14 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.1405 | 100 | 1.5 | 100 | 2 | 100 | 2.8396 | 90.62 | 0 | 0 | 0 | 0 | 0
5 | 6 | 15 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.99456 | 100 | 1.5 | 100 | 2 | 100 | 2.9855 | 95.2768 | 0 | 0 | 0 | 0 | 0
5 | 6 | 16 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.7872 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.059359 | 1.3191 | 0 | 0 | 0
5 | 6 | 17 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.52608 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.32048 | 7.1218 | 0 | 0 | 0
5 | 6 | 18 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.2592 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.58736 | 13.0524 | 0 | 0 | 0
5 | 6 | 19 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.05376 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.7928 | 17.6178 | 0 | 0 | 0
5 | 6 | 20 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 6 | 21 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 6 | 22 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 6 | 23 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 6 | 24 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 7 | 1 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 7 | 2 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 7 | 3 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 7 | 4 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 7 | 5 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 7 | 6 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 7 | 7 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.03648 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.81008 | 18.0018 | 0 | 0 | 0
5 | 7 | 8 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.18816 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.6584 | 14.6311 | 0 | 0 | 0
5 | 7 | 9 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.40896 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.4376 | 9.7244 | 0 | 0 | 0
5 | 7 | 10 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.64704 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.19952 | 4.4338 | 0 | 0 | 0
5 | 7 | 11 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.84672 | 100 | 1.5 | 100 | 2 | 100 | 3.1333 | 99.9949 | 0 | 0 | 0 | 0 | 0
5 | 7 | 12 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.9888 | 100 | 1.5 | 100 | 2 | 100 | 2.9913 | 95.4606 | 0 | 0 | 0 | 0 | 0
5 | 7 | 13 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.0406 | 100 | 1.5 | 100 | 2 | 100 | 2.9394 | 93.8063 | 0 | 0 | 0 | 0 | 0
5 | 7 | 14 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.008 | 100 | 1.5 | 100 | 2 | 100 | 2.9721 | 94.8479 | 0 | 0 | 0 | 0 | 0
5 | 7 | 15 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.8928 | 100 | 1.5 | 100 | 2 | 100 | 3.0873 | 98.5243 | 0 | 0 | 0 | 0 | 0
5 | 7 | 16 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.69504 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.15152 | 3.3671 | 0 | 0 | 0
5 | 7 | 17 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.46656 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.38 | 8.4444 | 0 | 0 | 0
5 | 7 | 18 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.23808 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.60848 | 13.5218 | 0 | 0 | 0
5 | 7 | 19 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.05568 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.79088 | 17.5751 | 0 | 0 | 0
5 | 7 | 20 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 7 | 21 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 7 | 22 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 7 | 23 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 7 | 24 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 8 | 1 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 8 | 2 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 8 | 3 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 8 | 4 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 8 | 5 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 8 | 6 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 8 | 7 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.02112 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.82544 | 18.3431 | 0 | 0 | 0
5 | 8 | 8 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.19392 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.65264 | 14.5031 | 0 | 0 | 0
5 | 8 | 9 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.44544 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.40112 | 8.9138 | 0 | 0 | 0
5 | 8 | 10 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.70464 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.14192 | 3.1538 | 0 | 0 | 0
5 | 8 | 11 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.9216 | 100 | 1.5 | 100 | 2 | 100 | 3.0585 | 97.6052 | 0 | 0 | 0 | 0 | 0
5 | 8 | 12 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.0694 | 100 | 1.5 | 100 | 2 | 100 | 2.9106 | 92.8872 | 0 | 0 | 0 | 0 | 0
5 | 8 | 13 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.1309 | 100 | 1.5 | 100 | 2 | 100 | 2.8492 | 90.9264 | 0 | 0 | 0 | 0 | 0
5 | 8 | 14 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.0771 | 100 | 1.5 | 100 | 2 | 100 | 2.9029 | 92.6421 | 0 | 0 | 0 | 0 | 0
5 | 8 | 15 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.9504 | 100 | 1.5 | 100 | 2 | 100 | 3.0297 | 96.6861 | 0 | 0 | 0 | 0 | 0
5 | 8 | 16 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.73536 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.1112 | 2.4711 | 0 | 0 | 0
5 | 8 | 17 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.48 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.36656 | 8.1458 | 0 | 0 | 0
5 | 8 | 18 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.2208 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.62576 | 13.9058 | 0 | 0 | 0
5 | 8 | 19 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.02688 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.81968 | 18.2151 | 0 | 0 | 0
5 | 8 | 20 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 8 | 21 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 8 | 22 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 8 | 23 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 8 | 24 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 9 | 1 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 9 | 2 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 9 | 3 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 9 | 4 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 9 | 5 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 9 | 6 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 9 | 7 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.01728 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.82928 | 18.4284 | 0 | 0 | 0
5 | 9 | 8 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.2496 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.59696 | 13.2658 | 0 | 0 | 0
5 | 9 | 9 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.5952 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.25136 | 5.5858 | 0 | 0 | 0
5 | 9 | 10 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.912 | 100 | 1.5 | 100 | 2 | 100 | 3.0681 | 97.9116 | 0 | 0 | 0 | 0 | 0
5 | 9 | 11 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.152 | 100 | 1.5 | 100 | 2 | 100 | 2.8281 | 90.2524 | 0 | 0 | 0 | 0 | 0
5 | 9 | 12 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.3018 | 100 | 1.5 | 100 | 2 | 100 | 2.6783 | 85.4731 | 0 | 0 | 0 | 0 | 0
5 | 9 | 13 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.3459 | 100 | 1.5 | 100 | 2 | 100 | 2.6341 | 84.0638 | 0 | 0 | 0 | 0 | 0
5 | 9 | 14 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.2691 | 100 | 1.5 | 100 | 2 | 100 | 2.7109 | 86.5147 | 0 | 0 | 0 | 0 | 0
5 | 9 | 15 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.081 | 100 | 1.5 | 100 | 2 | 100 | 2.8991 | 92.5195 | 0 | 0 | 0 | 0 | 0
5 | 9 | 16 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.82944 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.017119 | 0.38042 | 0 | 0 | 0
5 | 9 | 17 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.50688 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.33968 | 7.5484 | 0 | 0 | 0
5 | 9 | 18 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.16512 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.68144 | 15.1431 | 0 | 0 | 0
5 | 9 | 19 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.00192 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84464 | 18.7698 | 0 | 0 | 0
5 | 9 | 20 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 9 | 21 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 9 | 22 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 9 | 23 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 9 | 24 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 10 | 1 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 10 | 2 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 10 | 3 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 10 | 4 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 10 | 5 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 10 | 6 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 10 | 7 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 10 | 8 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.26304 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.58352 | 12.9671 | 0 | 0 | 0
5 | 10 | 9 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.70272 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.14384 | 3.1964 | 0 | 0 | 0
5 | 10 | 10 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.0406 | 100 | 1.5 | 100 | 2 | 100 | 2.9394 | 93.8063 | 0 | 0 | 0 | 0 | 0
5 | 10 | 11 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.2845 | 100 | 1.5 | 100 | 2 | 100 | 2.6956 | 86.0245 | 0 | 0 | 0 | 0 | 0
5 | 10 | 12 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.4246 | 100 | 1.5 | 100 | 2 | 100 | 2.5554 | 81.5516 | 0 | 0 | 0 | 0 | 0
5 | 10 | 13 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.4477 | 100 | 1.5 | 100 | 2 | 100 | 2.5324 | 80.8163 | 0 | 0 | 0 | 0 | 0
5 | 10 | 14 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.3344 | 100 | 1.5 | 100 | 2 | 100 | 2.6457 | 84.4314 | 0 | 0 | 0 | 0 | 0
5 | 10 | 15 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.1194 | 100 | 1.5 | 100 | 2 | 100 | 2.8607 | 91.294 | 0 | 0 | 0 | 0 | 0
5 | 10 | 16 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.81984 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.026719 | 0.59375 | 0 | 0 | 0
5 | 10 | 17 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.45888 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.38768 | 8.6151 | 0 | 0 | 0
5 | 10 | 18 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.05952 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.78704 | 17.4898 | 0 | 0 | 0
5 | 10 | 19 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 10 | 20 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 10 | 21 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 10 | 22 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 10 | 23 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 10 | 24 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 11 | 1 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 11 | 2 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 11 | 3 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 11 | 4 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 11 | 5 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 11 | 6 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 11 | 7 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 11 | 8 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.15552 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.69104 | 15.3564 | 0 | 0 | 0
5 | 11 | 9 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.63168 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.21488 | 4.7751 | 0 | 0 | 0
5 | 11 | 10 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.9888 | 100 | 1.5 | 100 | 2 | 100 | 2.9913 | 95.4606 | 0 | 0 | 0 | 0 | 0
5 | 11 | 11 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.2365 | 100 | 1.5 | 100 | 2 | 100 | 2.7436 | 87.5564 | 0 | 0 | 0 | 0 | 0
5 | 11 | 12 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.3728 | 100 | 1.5 | 100 | 2 | 100 | 2.6073 | 83.206 | 0 | 0 | 0 | 0 | 0
5 | 11 | 13 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.3862 | 100 | 1.5 | 100 | 2 | 100 | 2.5938 | 82.7771 | 0 | 0 | 0 | 0 | 0
5 | 11 | 14 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.2902 | 100 | 1.5 | 100 | 2 | 100 | 2.6898 | 85.8407 | 0 | 0 | 0 | 0 | 0
5 | 11 | 15 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.0752 | 100 | 1.5 | 100 | 2 | 100 | 2.9049 | 92.7033 | 0 | 0 | 0 | 0 | 0
5 | 11 | 16 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.77184 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.074719 | 1.6604 | 0 | 0 | 0
5 | 11 | 17 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.336 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.51056 | 11.3458 | 0 | 0 | 0
5 | 11 | 18 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 11 | 19 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 11 | 20 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 11 | 21 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 11 | 22 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 11 | 23 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 11 | 24 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 12 | 1 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 12 | 2 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 12 | 3 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 12 | 4 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 12 | 5 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 12 | 6 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 12 | 7 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 12 | 8 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.06336 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.7832 | 17.4044 | 0 | 0 | 0
5 | 12 | 9 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.52416 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.3224 | 7.1644 | 0 | 0 | 0
5 | 12 | 10 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.89664 | 100 | 1.5 | 100 | 2 | 100 | 3.0834 | 98.4018 | 0 | 0 | 0 | 0 | 0
5 | 12 | 11 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.1635 | 100 | 1.5 | 100 | 2 | 100 | 2.8165 | 89.8848 | 0 | 0 | 0 | 0 | 0
5 | 12 | 12 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.3267 | 100 | 1.5 | 100 | 2 | 100 | 2.6533 | 84.6765 | 0 | 0 | 0 | 0 | 0
5 | 12 | 13 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.3709 | 100 | 1.5 | 100 | 2 | 100 | 2.6092 | 83.2672 | 0 | 0 | 0 | 0 | 0
5 | 12 | 14 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.2883 | 100 | 1.5 | 100 | 2 | 100 | 2.6917 | 85.902 | 0 | 0 | 0 | 0 | 0
5 | 12 | 15 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 1.0906 | 100 | 1.5 | 100 | 2 | 100 | 2.8895 | 92.2131 | 0 | 0 | 0 | 0 | 0
5 | 12 | 16 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.80448 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.042079 | 0.93509 | 0 | 0 | 0
5 | 12 | 17 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.37056 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.476 | 10.5778 | 0 | 0 | 0
5 | 12 | 18 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0.00384 | 100 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84272 | 18.7271 | 0 | 0 | 0
5 | 12 | 19 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 12 | 20 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 12 | 21 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 12 | 22 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 12 | 23 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
5 | 12 | 24 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
6 | 1 | 1 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 1 | 2 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 1 | 3 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 1 | 4 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 1 | 5 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 1 | 6 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 1 | 7 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 1 | 8 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.041888 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.86329 | 19.1842 | 0 | 0 | 0
6 | 1 | 9 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.45696 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.44822 | 9.9604 | 0 | 0 | 0
6 | 1 | 10 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.84347 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.061707 | 1.3713 | 0 | 0 | 0
6 | 1 | 11 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.1348 | 100 | 1.5 | 100 | 2 | 100 | 2.8544 | 92.555 | 0 | 0 | 0 | 0 | 0
6 | 1 | 12 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.3233 | 100 | 1.5 | 100 | 2 | 100 | 2.6659 | 86.4429 | 0 | 0 | 0 | 0 | 0
6 | 1 | 13 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.3937 | 100 | 1.5 | 100 | 2 | 100 | 2.5955 | 84.1586 | 0 | 0 | 0 | 0 | 0
6 | 1 | 14 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.3404 | 100 | 1.5 | 100 | 2 | 100 | 2.6488 | 85.8873 | 0 | 0 | 0 | 0 | 0
6 | 1 | 15 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.1748 | 100 | 1.5 | 100 | 2 | 100 | 2.8144 | 91.2585 | 0 | 0 | 0 | 0 | 0
6 | 1 | 16 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.89678 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.0083952 | 0.18656 | 0 | 0 | 0
6 | 1 | 17 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.54074 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.36444 | 8.0987 | 0 | 0 | 0
6 | 1 | 18 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.07616 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.82902 | 18.4226 | 0 | 0 | 0
6 | 1 | 19 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 1 | 20 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 1 | 21 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 1 | 22 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 1 | 23 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 1 | 24 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 2 | 1 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 2 | 2 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 2 | 3 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 2 | 4 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 2 | 5 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 2 | 6 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 2 | 7 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 2 | 8 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.068544 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.83664 | 18.5919 | 0 | 0 | 0
6 | 2 | 9 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.49885 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.40633 | 9.0296 | 0 | 0 | 0
6 | 2 | 10 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.88536 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.019819 | 0.44043 | 0 | 0 | 0
6 | 2 | 11 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.1881 | 100 | 1.5 | 100 | 2 | 100 | 2.8011 | 90.8263 | 0 | 0 | 0 | 0 | 0
6 | 2 | 12 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.3918 | 100 | 1.5 | 100 | 2 | 100 | 2.5974 | 84.2203 | 0 | 0 | 0 | 0 | 0
6 | 2 | 13 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.4718 | 100 | 1.5 | 100 | 2 | 100 | 2.5174 | 81.6273 | 0 | 0 | 0 | 0 | 0
6 | 2 | 14 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.4337 | 100 | 1.5 | 100 | 2 | 100 | 2.5555 | 82.8621 | 0 | 0 | 0 | 0 | 0
6 | 2 | 15 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.2757 | 100 | 1.5 | 100 | 2 | 100 | 2.7135 | 87.9864 | 0 | 0 | 0 | 0 | 0
6 | 2 | 16 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.0129 | 100 | 1.5 | 100 | 2 | 100 | 2.9763 | 96.5062 | 0 | 0 | 0 | 0 | 0
6 | 2 | 17 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.66069 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.24449 | 5.4331 | 0 | 0 | 0
6 | 2 | 18 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.17326 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.73192 | 16.2648 | 0 | 0 | 0
6 | 2 | 19 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 2 | 20 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 2 | 21 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 2 | 22 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 2 | 23 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 2 | 24 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 3 | 1 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 3 | 2 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 3 | 3 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 3 | 4 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 3 | 5 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 3 | 6 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 3 | 7 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.001904 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90328 | 20.0728 | 0 | 0 | 0
6 | 3 | 8 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.15803 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.74715 | 16.6033 | 0 | 0 | 0
6 | 3 | 9 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.5731 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.33208 | 7.3794 | 0 | 0 | 0
6 | 3 | 10 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.94438 | 100 | 1.5 | 100 | 2 | 100 | 3.0448 | 98.7288 | 0 | 0 | 0 | 0 | 0
6 | 3 | 11 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.2224 | 100 | 1.5 | 100 | 2 | 100 | 2.7668 | 89.715 | 0 | 0 | 0 | 0 | 0
6 | 3 | 12 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.4147 | 100 | 1.5 | 100 | 2 | 100 | 2.5745 | 83.4795 | 0 | 0 | 0 | 0 | 0
6 | 3 | 13 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.487 | 100 | 1.5 | 100 | 2 | 100 | 2.5022 | 81.1334 | 0 | 0 | 0 | 0 | 0
6 | 3 | 14 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.4528 | 100 | 1.5 | 100 | 2 | 100 | 2.5364 | 82.2447 | 0 | 0 | 0 | 0 | 0
6 | 3 | 15 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.2585 | 100 | 1.5 | 100 | 2 | 100 | 2.7306 | 88.542 | 0 | 0 | 0 | 0 | 0
6 | 3 | 16 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.9977 | 100 | 1.5 | 100 | 2 | 100 | 2.9915 | 97.0001 | 0 | 0 | 0 | 0 | 0
6 | 3 | 17 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.65307 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.25211 | 5.6024 | 0 | 0 | 0
6 | 3 | 18 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.24562 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.65956 | 14.657 | 0 | 0 | 0
6 | 3 | 19 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.001904 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90328 | 20.0728 | 0 | 0 | 0
6 | 3 | 20 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 3 | 21 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 3 | 22 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 3 | 23 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 3 | 24 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 4 | 1 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 4 | 2 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 4 | 3 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 4 | 4 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 4 | 5 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 4 | 6 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 4 | 7 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.02856 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.87662 | 19.4804 | 0 | 0 | 0
6 | 4 | 8 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.27608 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.6291 | 13.98 | 0 | 0 | 0
6 | 4 | 9 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.63594 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.26924 | 5.9832 | 0 | 0 | 0
6 | 4 | 10 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.96723 | 100 | 1.5 | 100 | 2 | 100 | 3.0219 | 97.9879 | 0 | 0 | 0 | 0 | 0
6 | 4 | 11 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.2167 | 100 | 1.5 | 100 | 2 | 100 | 2.7725 | 89.9002 | 0 | 0 | 0 | 0 | 0
6 | 4 | 12 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.369 | 100 | 1.5 | 100 | 2 | 100 | 2.6202 | 84.9612 | 0 | 0 | 0 | 0 | 0
6 | 4 | 13 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.4166 | 100 | 1.5 | 100 | 2 | 100 | 2.5726 | 83.4177 | 0 | 0 | 0 | 0 | 0
6 | 4 | 14 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.3461 | 100 | 1.5 | 100 | 2 | 100 | 2.6431 | 85.702 | 0 | 0 | 0 | 0 | 0
6 | 4 | 15 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.1767 | 100 | 1.5 | 100 | 2 | 100 | 2.8125 | 91.1967 | 0 | 0 | 0 | 0 | 0
6 | 4 | 16 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.91392 | 100 | 1.5 | 100 | 2 | 100 | 3.0753 | 99.7166 | 0 | 0 | 0 | 0 | 0
6 | 4 | 17 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.59786 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.30732 | 6.8294 | 0 | 0 | 0
6 | 4 | 18 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.25133 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.65385 | 14.53 | 0 | 0 | 0
6 | 4 | 19 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.01904 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.88614 | 19.692 | 0 | 0 | 0
6 | 4 | 20 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 4 | 21 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 4 | 22 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 4 | 23 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 4 | 24 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 5 | 1 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 5 | 2 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 5 | 3 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 5 | 4 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 5 | 5 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 5 | 6 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 5 | 7 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.068544 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.83664 | 18.5919 | 0 | 0 | 0
6 | 5 | 8 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.30464 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.60054 | 13.3453 | 0 | 0 | 0
6 | 5 | 9 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.6207 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.28448 | 6.3217 | 0 | 0 | 0
6 | 5 | 10 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.91773 | 100 | 1.5 | 100 | 2 | 100 | 3.0715 | 99.5931 | 0 | 0 | 0 | 0 | 0
6 | 5 | 11 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.1424 | 100 | 1.5 | 100 | 2 | 100 | 2.8468 | 92.308 | 0 | 0 | 0 | 0 | 0
6 | 5 | 12 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.2814 | 100 | 1.5 | 100 | 2 | 100 | 2.7078 | 87.8011 | 0 | 0 | 0 | 0 | 0
6 | 5 | 13 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.3195 | 100 | 1.5 | 100 | 2 | 100 | 2.6697 | 86.5664 | 0 | 0 | 0 | 0 | 0
6 | 5 | 14 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.2528 | 100 | 1.5 | 100 | 2 | 100 | 2.7363 | 88.7272 | 0 | 0 | 0 | 0 | 0
6 | 5 | 15 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.0929 | 100 | 1.5 | 100 | 2 | 100 | 2.8963 | 93.9132 | 0 | 0 | 0 | 0 | 0
6 | 5 | 16 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.85109 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.054091 | 1.202 | 0 | 0 | 0
6 | 5 | 17 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.55216 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.35302 | 7.8449 | 0 | 0 | 0
6 | 5 | 18 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.25514 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.65004 | 14.4454 | 0 | 0 | 0
6 | 5 | 19 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.036176 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.869 | 19.3112 | 0 | 0 | 0
6 | 5 | 20 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 5 | 21 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 5 | 22 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 5 | 23 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 5 | 24 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 6 | 1 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 6 | 2 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 6 | 3 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 6 | 4 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 6 | 5 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 6 | 6 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 6 | 7 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.06664 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.83854 | 18.6342 | 0 | 0 | 0
6 | 6 | 8 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.25133 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.65385 | 14.53 | 0 | 0 | 0
6 | 6 | 9 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.51598 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.3892 | 8.6488 | 0 | 0 | 0
6 | 6 | 10 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.78826 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.11692 | 2.5983 | 0 | 0 | 0
6 | 6 | 11 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.0034 | 100 | 1.5 | 100 | 2 | 100 | 2.9858 | 96.8149 | 0 | 0 | 0 | 0 | 0
6 | 6 | 12 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.1329 | 100 | 1.5 | 100 | 2 | 100 | 2.8563 | 92.6167 | 0 | 0 | 0 | 0 | 0
6 | 6 | 13 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.1862 | 100 | 1.5 | 100 | 2 | 100 | 2.803 | 90.888 | 0 | 0 | 0 | 0 | 0
6 | 6 | 14 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.131 | 100 | 1.5 | 100 | 2 | 100 | 2.8582 | 92.6784 | 0 | 0 | 0 | 0 | 0
6 | 6 | 15 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.98627 | 100 | 1.5 | 100 | 2 | 100 | 3.0029 | 97.3705 | 0 | 0 | 0 | 0 | 0
6 | 6 | 16 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.78064 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.12454 | 2.7675 | 0 | 0 | 0
6 | 6 | 17 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.5217 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.38348 | 8.5218 | 0 | 0 | 0
6 | 6 | 18 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.25704 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.64814 | 14.4031 | 0 | 0 | 0
6 | 6 | 19 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.053312 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.85187 | 18.9304 | 0 | 0 | 0
6 | 6 | 20 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 6 | 21 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 6 | 22 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 6 | 23 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 6 | 24 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 7 | 1 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 7 | 2 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 7 | 3 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 7 | 4 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 7 | 5 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 7 | 6 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 7 | 7 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.036176 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.869 | 19.3112 | 0 | 0 | 0
6 | 7 | 8 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.18659 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.71859 | 15.9686 | 0 | 0 | 0
6 | 7 | 9 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.40555 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.49963 | 11.1028 | 0 | 0 | 0
6 | 7 | 10 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.64165 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.26353 | 5.8562 | 0 | 0 | 0
6 | 7 | 11 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.83966 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.065515 | 1.4559 | 0 | 0 | 0
6 | 7 | 12 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.98056 | 100 | 1.5 | 100 | 2 | 100 | 3.0086 | 97.5557 | 0 | 0 | 0 | 0 | 0
6 | 7 | 13 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.032 | 100 | 1.5 | 100 | 2 | 100 | 2.9572 | 95.8888 | 0 | 0 | 0 | 0 | 0
6 | 7 | 14 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.9996 | 100 | 1.5 | 100 | 2 | 100 | 2.9896 | 96.9384 | 0 | 0 | 0 | 0 | 0
6 | 7 | 15 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.88536 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.019819 | 0.44043 | 0 | 0 | 0
6 | 7 | 16 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.68925 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.21593 | 4.7985 | 0 | 0 | 0
6 | 7 | 17 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.46267 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.44251 | 9.8335 | 0 | 0 | 0
6 | 7 | 18 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.2361 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.66908 | 14.8685 | 0 | 0 | 0
6 | 7 | 19 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.055216 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.84996 | 18.8881 | 0 | 0 | 0
6 | 7 | 20 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 7 | 21 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 7 | 22 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 7 | 23 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 7 | 24 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 8 | 1 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 8 | 2 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 8 | 3 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 8 | 4 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 8 | 5 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 8 | 6 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 8 | 7 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.020944 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.88424 | 19.6497 | 0 | 0 | 0
6 | 8 | 8 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.1923 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.71288 | 15.8417 | 0 | 0 | 0
6 | 8 | 9 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.44173 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.46345 | 10.2989 | 0 | 0 | 0
6 | 8 | 10 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.69877 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.20641 | 4.5869 | 0 | 0 | 0
6 | 8 | 11 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.91392 | 100 | 1.5 | 100 | 2 | 100 | 3.0753 | 99.7166 | 0 | 0 | 0 | 0 | 0
6 | 8 | 12 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.0605 | 100 | 1.5 | 100 | 2 | 100 | 2.9287 | 94.9627 | 0 | 0 | 0 | 0 | 0
6 | 8 | 13 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.1215 | 100 | 1.5 | 100 | 2 | 100 | 2.8677 | 92.9871 | 0 | 0 | 0 | 0 | 0
6 | 8 | 14 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.0681 | 100 | 1.5 | 100 | 2 | 100 | 2.921 | 94.7158 | 0 | 0 | 0 | 0 | 0
6 | 8 | 15 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.94248 | 100 | 1.5 | 100 | 2 | 100 | 3.0467 | 98.7905 | 0 | 0 | 0 | 0 | 0
6 | 8 | 16 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.72923 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.17595 | 3.9099 | 0 | 0 | 0
6 | 8 | 17 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.476 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.42918 | 9.5373 | 0 | 0 | 0
6 | 8 | 18 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.21896 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.68622 | 15.2493 | 0 | 0 | 0
6 | 8 | 19 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.026656 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.87852 | 19.5227 | 0 | 0 | 0
6 | 8 | 20 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 8 | 21 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 8 | 22 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 8 | 23 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 8 | 24 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 9 | 1 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 9 | 2 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 9 | 3 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 9 | 4 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 9 | 5 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 9 | 6 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 9 | 7 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.017136 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.88804 | 19.7343 | 0 | 0 | 0
6 | 9 | 8 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.24752 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.65766 | 14.6146 | 0 | 0 | 0
6 | 9 | 9 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.59024 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.31494 | 6.9986 | 0 | 0 | 0
6 | 9 | 10 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.9044 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.00077917 | 0.017315 | 0 | 0 | 0
6 | 9 | 11 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.1424 | 100 | 1.5 | 100 | 2 | 100 | 2.8468 | 92.308 | 0 | 0 | 0 | 0 | 0
6 | 9 | 12 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.2909 | 100 | 1.5 | 100 | 2 | 100 | 2.6983 | 87.4925 | 0 | 0 | 0 | 0 | 0
6 | 9 | 13 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.3347 | 100 | 1.5 | 100 | 2 | 100 | 2.6545 | 86.0725 | 0 | 0 | 0 | 0 | 0
6 | 9 | 14 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.2585 | 100 | 1.5 | 100 | 2 | 100 | 2.7306 | 88.542 | 0 | 0 | 0 | 0 | 0
6 | 9 | 15 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.072 | 100 | 1.5 | 100 | 2 | 100 | 2.9172 | 94.5923 | 0 | 0 | 0 | 0 | 0
6 | 9 | 16 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.82253 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.082651 | 1.8367 | 0 | 0 | 0
6 | 9 | 17 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.50266 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.40252 | 8.945 | 0 | 0 | 0
6 | 9 | 18 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.16374 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.74144 | 16.4763 | 0 | 0 | 0
6 | 9 | 19 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.001904 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90328 | 20.0728 | 0 | 0 | 0
6 | 9 | 20 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 9 | 21 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 9 | 22 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 9 | 23 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 9 | 24 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 10 | 1 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 10 | 2 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 10 | 3 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 10 | 4 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 10 | 5 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 10 | 6 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 10 | 7 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 10 | 8 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.26085 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.64433 | 14.3185 | 0 | 0 | 0
6 | 10 | 9 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.69686 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.20832 | 4.6292 | 0 | 0 | 0
6 | 10 | 10 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.032 | 100 | 1.5 | 100 | 2 | 100 | 2.9572 | 95.8888 | 0 | 0 | 0 | 0 | 0
6 | 10 | 11 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.2738 | 100 | 1.5 | 100 | 2 | 100 | 2.7154 | 88.0481 | 0 | 0 | 0 | 0 | 0
6 | 10 | 12 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.4128 | 100 | 1.5 | 100 | 2 | 100 | 2.5764 | 83.5412 | 0 | 0 | 0 | 0 | 0
6 | 10 | 13 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.4356 | 100 | 1.5 | 100 | 2 | 100 | 2.5536 | 82.8004 | 0 | 0 | 0 | 0 | 0
6 | 10 | 14 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.3233 | 100 | 1.5 | 100 | 2 | 100 | 2.6659 | 86.4429 | 0 | 0 | 0 | 0 | 0
6 | 10 | 15 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.11 | 100 | 1.5 | 100 | 2 | 100 | 2.8791 | 93.3576 | 0 | 0 | 0 | 0 | 0
6 | 10 | 16 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.81301 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.092171 | 2.0482 | 0 | 0 | 0
6 | 10 | 17 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.45506 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.45012 | 10.0027 | 0 | 0 | 0
6 | 10 | 18 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.059024 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.84616 | 18.8034 | 0 | 0 | 0
6 | 10 | 19 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 10 | 20 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 10 | 21 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 10 | 22 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 10 | 23 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 10 | 24 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 11 | 1 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 11 | 2 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 11 | 3 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 11 | 4 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 11 | 5 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 11 | 6 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 11 | 7 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 11 | 8 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.15422 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.75096 | 16.6879 | 0 | 0 | 0
6 | 11 | 9 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.62642 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.27876 | 6.1947 | 0 | 0 | 0
6 | 11 | 10 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.98056 | 100 | 1.5 | 100 | 2 | 100 | 3.0086 | 97.5557 | 0 | 0 | 0 | 0 | 0
6 | 11 | 11 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.2262 | 100 | 1.5 | 100 | 2 | 100 | 2.763 | 89.5915 | 0 | 0 | 0 | 0 | 0
6 | 11 | 12 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.3614 | 100 | 1.5 | 100 | 2 | 100 | 2.6278 | 85.2081 | 0 | 0 | 0 | 0 | 0
6 | 11 | 13 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.3747 | 100 | 1.5 | 100 | 2 | 100 | 2.6145 | 84.776 | 0 | 0 | 0 | 0 | 0
6 | 11 | 14 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.2795 | 100 | 1.5 | 100 | 2 | 100 | 2.7097 | 87.8629 | 0 | 0 | 0 | 0 | 0
6 | 11 | 15 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.0662 | 100 | 1.5 | 100 | 2 | 100 | 2.9229 | 94.7775 | 0 | 0 | 0 | 0 | 0
6 | 11 | 16 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.76541 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.13977 | 3.106 | 0 | 0 | 0
6 | 11 | 17 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.3332 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.57198 | 12.7106 | 0 | 0 | 0
6 | 11 | 18 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 11 | 19 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 11 | 20 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 11 | 21 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 11 | 22 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 11 | 23 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 11 | 24 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 12 | 1 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 12 | 2 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 12 | 3 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 12 | 4 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 12 | 5 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 12 | 6 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 12 | 7 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 12 | 8 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.062832 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.84235 | 18.7188 | 0 | 0 | 0
6 | 12 | 9 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.51979 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.38539 | 8.5642 | 0 | 0 | 0
6 | 12 | 10 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.88917 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.016011 | 0.3558 | 0 | 0 | 0
6 | 12 | 11 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.1538 | 100 | 1.5 | 100 | 2 | 100 | 2.8354 | 91.9376 | 0 | 0 | 0 | 0 | 0
6 | 12 | 12 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.3157 | 100 | 1.5 | 100 | 2 | 100 | 2.6735 | 86.6899 | 0 | 0 | 0 | 0 | 0
6 | 12 | 13 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.3595 | 100 | 1.5 | 100 | 2 | 100 | 2.6297 | 85.2699 | 0 | 0 | 0 | 0 | 0
6 | 12 | 14 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.2776 | 100 | 1.5 | 100 | 2 | 100 | 2.7116 | 87.9246 | 0 | 0 | 0 | 0 | 0
6 | 12 | 15 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 1.0815 | 100 | 1.5 | 100 | 2 | 100 | 2.9077 | 94.2836 | 0 | 0 | 0 | 0 | 0
6 | 12 | 16 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.79778 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.1074 | 2.3867 | 0 | 0 | 0
6 | 12 | 17 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.36747 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.53771 | 11.949 | 0 | 0 | 0
6 | 12 | 18 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0.003808 | 100 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90137 | 20.0305 | 0 | 0 | 0
6 | 12 | 19 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 12 | 20 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 12 | 21 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 12 | 22 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 12 | 23 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
6 | 12 | 24 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
7 | 1 | 1 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 1 | 2 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 1 | 3 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 1 | 4 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 1 | 5 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 1 | 6 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 1 | 7 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 1 | 8 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.041536 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.92226 | 20.4947 | 0 | 0 | 0
7 | 1 | 9 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.45312 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.51068 | 11.3484 | 0 | 0 | 0
7 | 1 | 10 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.83638 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.12742 | 2.8315 | 0 | 0 | 0
7 | 1 | 11 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.1252 | 100 | 1.5 | 100 | 2 | 100 | 2.8731 | 94.6796 | 0 | 0 | 0 | 0 | 0
7 | 1 | 12 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.3122 | 100 | 1.5 | 100 | 2 | 100 | 2.6861 | 88.52 | 0 | 0 | 0 | 0 | 0
7 | 1 | 13 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.382 | 100 | 1.5 | 100 | 2 | 100 | 2.6163 | 86.2179 | 0 | 0 | 0 | 0 | 0
7 | 1 | 14 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.3292 | 100 | 1.5 | 100 | 2 | 100 | 2.6691 | 87.96 | 0 | 0 | 0 | 0 | 0
7 | 1 | 15 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.1649 | 100 | 1.5 | 100 | 2 | 100 | 2.8334 | 93.373 | 0 | 0 | 0 | 0 | 0
7 | 1 | 16 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.88925 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.074551 | 1.6567 | 0 | 0 | 0
7 | 1 | 17 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.53619 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.42761 | 9.5024 | 0 | 0 | 0
7 | 1 | 18 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.07552 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.88828 | 19.7395 | 0 | 0 | 0
7 | 1 | 19 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 1 | 20 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 1 | 21 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 1 | 22 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 1 | 23 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 1 | 24 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 2 | 1 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 2 | 2 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 2 | 3 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 2 | 4 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 2 | 5 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 2 | 6 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 2 | 7 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 2 | 8 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.067968 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.89583 | 19.9074 | 0 | 0 | 0
7 | 2 | 9 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.49466 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.46914 | 10.4254 | 0 | 0 | 0
7 | 2 | 10 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.87792 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.085879 | 1.9084 | 0 | 0 | 0
7 | 2 | 11 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.1781 | 100 | 1.5 | 100 | 2 | 100 | 2.8202 | 92.9375 | 0 | 0 | 0 | 0 | 0
7 | 2 | 12 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.3801 | 100 | 1.5 | 100 | 2 | 100 | 2.6182 | 86.2802 | 0 | 0 | 0 | 0 | 0
7 | 2 | 13 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.4594 | 100 | 1.5 | 100 | 2 | 100 | 2.5389 | 83.667 | 0 | 0 | 0 | 0 | 0
7 | 2 | 14 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.4217 | 100 | 1.5 | 100 | 2 | 100 | 2.5766 | 84.9114 | 0 | 0 | 0 | 0 | 0
7 | 2 | 15 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.265 | 100 | 1.5 | 100 | 2 | 100 | 2.7333 | 90.0754 | 0 | 0 | 0 | 0 | 0
7 | 2 | 16 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.0044 | 100 | 1.5 | 100 | 2 | 100 | 2.9939 | 98.6615 | 0 | 0 | 0 | 0 | 0
7 | 2 | 17 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.65514 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.30866 | 6.8592 | 0 | 0 | 0
7 | 2 | 18 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.17181 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.79199 | 17.5998 | 0 | 0 | 0
7 | 2 | 19 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 2 | 20 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 2 | 21 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 2 | 22 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 2 | 23 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 2 | 24 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 3 | 1 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 3 | 2 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 3 | 3 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 3 | 4 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 3 | 5 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 3 | 6 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 3 | 7 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.001888 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.96191 | 21.3758 | 0 | 0 | 0
7 | 3 | 8 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.1567 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.8071 | 17.9355 | 0 | 0 | 0
7 | 3 | 9 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.56829 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.39551 | 8.7891 | 0 | 0 | 0
7 | 3 | 10 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.93645 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.027351 | 0.60781 | 0 | 0 | 0
7 | 3 | 11 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.2121 | 100 | 1.5 | 100 | 2 | 100 | 2.7862 | 91.8175 | 0 | 0 | 0 | 0 | 0
7 | 3 | 12 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.4028 | 100 | 1.5 | 100 | 2 | 100 | 2.5955 | 85.5335 | 0 | 0 | 0 | 0 | 0
7 | 3 | 13 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.4745 | 100 | 1.5 | 100 | 2 | 100 | 2.5238 | 83.1693 | 0 | 0 | 0 | 0 | 0
7 | 3 | 14 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.4405 | 100 | 1.5 | 100 | 2 | 100 | 2.5578 | 84.2892 | 0 | 0 | 0 | 0 | 0
7 | 3 | 15 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.248 | 100 | 1.5 | 100 | 2 | 100 | 2.7503 | 90.6354 | 0 | 0 | 0 | 0 | 0
7 | 3 | 16 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.98931 | 100 | 1.5 | 100 | 2 | 100 | 3.009 | 99.1593 | 0 | 0 | 0 | 0 | 0
7 | 3 | 17 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.64758 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.31622 | 7.027 | 0 | 0 | 0
7 | 3 | 18 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.24355 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.72025 | 16.0055 | 0 | 0 | 0
7 | 3 | 19 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.001888 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.96191 | 21.3758 | 0 | 0 | 0
7 | 3 | 20 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 3 | 21 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 3 | 22 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 3 | 23 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 3 | 24 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 4 | 1 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 4 | 2 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 4 | 3 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 4 | 4 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 4 | 5 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 4 | 6 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 4 | 7 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.02832 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.93548 | 20.7884 | 0 | 0 | 0
7 | 4 | 8 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.27376 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.69004 | 15.3342 | 0 | 0 | 0
7 | 4 | 9 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.63059 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.33321 | 7.4046 | 0 | 0 | 0
7 | 4 | 10 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.9591 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.0046954 | 0.10434 | 0 | 0 | 0
7 | 4 | 11 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.2064 | 100 | 1.5 | 100 | 2 | 100 | 2.7919 | 92.0042 | 0 | 0 | 0 | 0 | 0
7 | 4 | 12 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.3575 | 100 | 1.5 | 100 | 2 | 100 | 2.6408 | 87.0268 | 0 | 0 | 0 | 0 | 0
7 | 4 | 13 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.4047 | 100 | 1.5 | 100 | 2 | 100 | 2.5936 | 85.4713 | 0 | 0 | 0 | 0 | 0
7 | 4 | 14 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.3348 | 100 | 1.5 | 100 | 2 | 100 | 2.6635 | 87.7734 | 0 | 0 | 0 | 0 | 0
7 | 4 | 15 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.1668 | 100 | 1.5 | 100 | 2 | 100 | 2.8315 | 93.3108 | 0 | 0 | 0 | 0 | 0
7 | 4 | 16 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.90624 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.057559 | 1.2791 | 0 | 0 | 0
7 | 4 | 17 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.59283 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.37097 | 8.2437 | 0 | 0 | 0
7 | 4 | 18 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.24922 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.71458 | 15.8796 | 0 | 0 | 0
7 | 4 | 19 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.01888 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.94492 | 20.9982 | 0 | 0 | 0
7 | 4 | 20 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 4 | 21 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 4 | 22 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 4 | 23 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 4 | 24 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 5 | 1 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 5 | 2 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 5 | 3 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 5 | 4 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 5 | 5 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 5 | 6 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 5 | 7 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.067968 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.89583 | 19.9074 | 0 | 0 | 0
7 | 5 | 8 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.30208 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.66172 | 14.7049 | 0 | 0 | 0
7 | 5 | 9 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.61549 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.34831 | 7.7403 | 0 | 0 | 0
7 | 5 | 10 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.91002 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.053783 | 1.1952 | 0 | 0 | 0
7 | 5 | 11 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.1328 | 100 | 1.5 | 100 | 2 | 100 | 2.8655 | 94.4307 | 0 | 0 | 0 | 0 | 0
7 | 5 | 12 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.2706 | 100 | 1.5 | 100 | 2 | 100 | 2.7277 | 89.8888 | 0 | 0 | 0 | 0 | 0
7 | 5 | 13 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.3084 | 100 | 1.5 | 100 | 2 | 100 | 2.6899 | 88.6444 | 0 | 0 | 0 | 0 | 0
7 | 5 | 14 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.2423 | 100 | 1.5 | 100 | 2 | 100 | 2.756 | 90.8221 | 0 | 0 | 0 | 0 | 0
7 | 5 | 15 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.0837 | 100 | 1.5 | 100 | 2 | 100 | 2.9146 | 96.0484 | 0 | 0 | 0 | 0 | 0
7 | 5 | 16 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.84394 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.11986 | 2.6636 | 0 | 0 | 0
7 | 5 | 17 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.54752 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.41628 | 9.2507 | 0 | 0 | 0
7 | 5 | 18 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.25299 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.71081 | 15.7957 | 0 | 0 | 0
7 | 5 | 19 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.035872 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.92793 | 20.6206 | 0 | 0 | 0
7 | 5 | 20 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 5 | 21 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 5 | 22 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 5 | 23 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 5 | 24 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 6 | 1 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 6 | 2 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 6 | 3 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 6 | 4 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 6 | 5 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 6 | 6 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 6 | 7 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.06608 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.89772 | 19.9493 | 0 | 0 | 0
7 | 6 | 8 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.24922 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.71458 | 15.8796 | 0 | 0 | 0
7 | 6 | 9 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.51165 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.45215 | 10.0478 | 0 | 0 | 0
7 | 6 | 10 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.78163 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.18217 | 4.0482 | 0 | 0 | 0
7 | 6 | 11 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.99498 | 100 | 1.5 | 100 | 2 | 100 | 3.0033 | 98.9726 | 0 | 0 | 0 | 0 | 0
7 | 6 | 12 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.1234 | 100 | 1.5 | 100 | 2 | 100 | 2.8749 | 94.7418 | 0 | 0 | 0 | 0 | 0
7 | 6 | 13 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.1762 | 100 | 1.5 | 100 | 2 | 100 | 2.8221 | 92.9997 | 0 | 0 | 0 | 0 | 0
7 | 6 | 14 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.1215 | 100 | 1.5 | 100 | 2 | 100 | 2.8768 | 94.804 | 0 | 0 | 0 | 0 | 0
7 | 6 | 15 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.97798 | 100 | 1.5 | 100 | 2 | 100 | 3.0203 | 99.5326 | 0 | 0 | 0 | 0 | 0
7 | 6 | 16 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.77408 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.18972 | 4.216 | 0 | 0 | 0
7 | 6 | 17 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.51731 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.44649 | 9.9219 | 0 | 0 | 0
7 | 6 | 18 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.25488 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.70892 | 15.7538 | 0 | 0 | 0
7 | 6 | 19 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.052864 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.91094 | 20.243 | 0 | 0 | 0
7 | 6 | 20 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 6 | 21 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 6 | 22 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 6 | 23 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 6 | 24 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 7 | 1 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 7 | 2 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 7 | 3 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 7 | 4 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 7 | 5 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 7 | 6 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 7 | 7 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.035872 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.92793 | 20.6206 | 0 | 0 | 0
7 | 7 | 8 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.18502 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.77878 | 17.3061 | 0 | 0 | 0
7 | 7 | 9 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.40214 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.56166 | 12.4812 | 0 | 0 | 0
7 | 7 | 10 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.63626 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.32754 | 7.2787 | 0 | 0 | 0
7 | 7 | 11 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.83261 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.13119 | 2.9154 | 0 | 0 | 0
7 | 7 | 12 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.97232 | 100 | 1.5 | 100 | 2 | 100 | 3.026 | 99.7192 | 0 | 0 | 0 | 0 | 0
7 | 7 | 13 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.0233 | 100 | 1.5 | 100 | 2 | 100 | 2.975 | 98.0393 | 0 | 0 | 0 | 0 | 0
7 | 7 | 14 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.9912 | 100 | 1.5 | 100 | 2 | 100 | 3.0071 | 99.097 | 0 | 0 | 0 | 0 | 0
7 | 7 | 15 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.87792 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.085879 | 1.9084 | 0 | 0 | 0
7 | 7 | 16 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.68346 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.28034 | 6.2299 | 0 | 0 | 0
7 | 7 | 17 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.45878 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.50502 | 11.2226 | 0 | 0 | 0
7 | 7 | 18 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.23411 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.72969 | 16.2153 | 0 | 0 | 0
7 | 7 | 19 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.054752 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.90905 | 20.2011 | 0 | 0 | 0
7 | 7 | 20 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 7 | 21 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 7 | 22 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 7 | 23 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 7 | 24 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 8 | 1 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 8 | 2 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 8 | 3 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 8 | 4 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 8 | 5 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 8 | 6 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 8 | 7 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.020768 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.94303 | 20.9563 | 0 | 0 | 0
7 | 8 | 8 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.19069 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.77311 | 17.1803 | 0 | 0 | 0
7 | 8 | 9 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.43802 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.52578 | 11.6841 | 0 | 0 | 0
7 | 8 | 10 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.6929 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.2709 | 6.0201 | 0 | 0 | 0
7 | 8 | 11 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.90624 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.057559 | 1.2791 | 0 | 0 | 0
7 | 8 | 12 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.0516 | 100 | 1.5 | 100 | 2 | 100 | 2.9467 | 97.1061 | 0 | 0 | 0 | 0 | 0
7 | 8 | 13 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.112 | 100 | 1.5 | 100 | 2 | 100 | 2.8863 | 95.1151 | 0 | 0 | 0 | 0 | 0
7 | 8 | 14 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.0592 | 100 | 1.5 | 100 | 2 | 100 | 2.9391 | 96.8572 | 0 | 0 | 0 | 0 | 0
7 | 8 | 15 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.93456 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.029239 | 0.64977 | 0 | 0 | 0
7 | 8 | 16 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.7231 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.2407 | 5.3488 | 0 | 0 | 0
7 | 8 | 17 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.472 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.4918 | 10.9289 | 0 | 0 | 0
7 | 8 | 18 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.21712 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.74668 | 16.5929 | 0 | 0 | 0
7 | 8 | 19 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.026432 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.93737 | 20.8304 | 0 | 0 | 0
7 | 8 | 20 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 8 | 21 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 8 | 22 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 8 | 23 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 8 | 24 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 9 | 1 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 9 | 2 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 9 | 3 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 9 | 4 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 9 | 5 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 9 | 6 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 9 | 7 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.016992 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.94681 | 21.0402 | 0 | 0 | 0
7 | 9 | 8 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.24544 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.71836 | 15.9635 | 0 | 0 | 0
7 | 9 | 9 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.58528 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.37852 | 8.4115 | 0 | 0 | 0
7 | 9 | 10 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.8968 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.066999 | 1.4889 | 0 | 0 | 0
7 | 9 | 11 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.1328 | 100 | 1.5 | 100 | 2 | 100 | 2.8655 | 94.4307 | 0 | 0 | 0 | 0 | 0
7 | 9 | 12 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.2801 | 100 | 1.5 | 100 | 2 | 100 | 2.7182 | 89.5777 | 0 | 0 | 0 | 0 | 0
7 | 9 | 13 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.3235 | 100 | 1.5 | 100 | 2 | 100 | 2.6748 | 88.1467 | 0 | 0 | 0 | 0 | 0
7 | 9 | 14 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.248 | 100 | 1.5 | 100 | 2 | 100 | 2.7503 | 90.6354 | 0 | 0 | 0 | 0 | 0
7 | 9 | 15 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.0629 | 100 | 1.5 | 100 | 2 | 100 | 2.9354 | 96.7328 | 0 | 0 | 0 | 0 | 0
7 | 9 | 16 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.81562 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.14818 | 3.293 | 0 | 0 | 0
7 | 9 | 17 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.49843 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.46537 | 10.3415 | 0 | 0 | 0
7 | 9 | 18 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.16237 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.80143 | 17.8096 | 0 | 0 | 0
7 | 9 | 19 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.001888 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.96191 | 21.3758 | 0 | 0 | 0
7 | 9 | 20 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 9 | 21 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 9 | 22 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 9 | 23 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 9 | 24 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 10 | 1 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 10 | 2 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 10 | 3 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 10 | 4 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 10 | 5 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 10 | 6 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 10 | 7 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 10 | 8 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.25866 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.70514 | 15.6699 | 0 | 0 | 0
7 | 10 | 9 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.69101 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.27279 | 6.062 | 0 | 0 | 0
7 | 10 | 10 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.0233 | 100 | 1.5 | 100 | 2 | 100 | 2.975 | 98.0393 | 0 | 0 | 0 | 0 | 0
7 | 10 | 11 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.2631 | 100 | 1.5 | 100 | 2 | 100 | 2.7352 | 90.1377 | 0 | 0 | 0 | 0 | 0
7 | 10 | 12 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.4009 | 100 | 1.5 | 100 | 2 | 100 | 2.5974 | 85.5958 | 0 | 0 | 0 | 0 | 0
7 | 10 | 13 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.4236 | 100 | 1.5 | 100 | 2 | 100 | 2.5747 | 84.8491 | 0 | 0 | 0 | 0 | 0
7 | 10 | 14 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.3122 | 100 | 1.5 | 100 | 2 | 100 | 2.6861 | 88.52 | 0 | 0 | 0 | 0 | 0
7 | 10 | 15 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.1007 | 100 | 1.5 | 100 | 2 | 100 | 2.8976 | 95.4884 | 0 | 0 | 0 | 0 | 0
7 | 10 | 16 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.80618 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.15762 | 3.5027 | 0 | 0 | 0
7 | 10 | 17 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.45123 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.51257 | 11.3904 | 0 | 0 | 0
7 | 10 | 18 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.058528 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.90527 | 20.1171 | 0 | 0 | 0
7 | 10 | 19 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 10 | 20 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 10 | 21 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 10 | 22 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 10 | 23 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 10 | 24 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 11 | 1 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 11 | 2 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 11 | 3 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 11 | 4 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 11 | 5 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 11 | 6 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 11 | 7 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 11 | 8 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.15293 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.81087 | 18.0194 | 0 | 0 | 0
7 | 11 | 9 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.62115 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.34265 | 7.6144 | 0 | 0 | 0
7 | 11 | 10 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.97232 | 100 | 1.5 | 100 | 2 | 100 | 3.026 | 99.7192 | 0 | 0 | 0 | 0 | 0
7 | 11 | 11 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.2159 | 100 | 1.5 | 100 | 2 | 100 | 2.7824 | 91.6931 | 0 | 0 | 0 | 0 | 0
7 | 11 | 12 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.3499 | 100 | 1.5 | 100 | 2 | 100 | 2.6484 | 87.2756 | 0 | 0 | 0 | 0 | 0
7 | 11 | 13 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.3631 | 100 | 1.5 | 100 | 2 | 100 | 2.6352 | 86.8401 | 0 | 0 | 0 | 0 | 0
7 | 11 | 14 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.2687 | 100 | 1.5 | 100 | 2 | 100 | 2.7296 | 89.951 | 0 | 0 | 0 | 0 | 0
7 | 11 | 15 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.0573 | 100 | 1.5 | 100 | 2 | 100 | 2.941 | 96.9194 | 0 | 0 | 0 | 0 | 0
7 | 11 | 16 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.75898 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.20482 | 4.5516 | 0 | 0 | 0
7 | 11 | 17 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.3304 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.6334 | 14.0755 | 0 | 0 | 0
7 | 11 | 18 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 11 | 19 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 11 | 20 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 11 | 21 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 11 | 22 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 11 | 23 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 11 | 24 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 12 | 1 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 12 | 2 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 12 | 3 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 12 | 4 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 12 | 5 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 12 | 6 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 12 | 7 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 12 | 8 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.062304 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9015 | 20.0332 | 0 | 0 | 0
7 | 12 | 9 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.51542 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.44838 | 9.9639 | 0 | 0 | 0
7 | 12 | 10 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.8817 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.082103 | 1.8245 | 0 | 0 | 0
7 | 12 | 11 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.1441 | 100 | 1.5 | 100 | 2 | 100 | 2.8542 | 94.0574 | 0 | 0 | 0 | 0 | 0
7 | 12 | 12 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.3046 | 100 | 1.5 | 100 | 2 | 100 | 2.6937 | 88.7689 | 0 | 0 | 0 | 0 | 0
7 | 12 | 13 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.348 | 100 | 1.5 | 100 | 2 | 100 | 2.6503 | 87.3379 | 0 | 0 | 0 | 0 | 0
7 | 12 | 14 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.2668 | 100 | 1.5 | 100 | 2 | 100 | 2.7315 | 90.0132 | 0 | 0 | 0 | 0 | 0
7 | 12 | 15 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 1.0724 | 100 | 1.5 | 100 | 2 | 100 | 2.9259 | 96.4217 | 0 | 0 | 0 | 0 | 0
7 | 12 | 16 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.79107 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.17273 | 3.8384 | 0 | 0 | 0
7 | 12 | 17 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.36438 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.59942 | 13.3203 | 0 | 0 | 0
7 | 12 | 18 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.003776 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.96002 | 21.3339 | 0 | 0 | 0
7 | 12 | 19 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 12 | 20 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 12 | 21 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 12 | 22 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 12 | 23 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
7 | 12 | 24 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.9638 | 21.4178 | 0 | 0 | 0
8 | 1 | 1 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 1 | 2 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 1 | 3 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 1 | 4 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 1 | 5 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 1 | 6 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 1 | 7 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 1 | 8 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.041184 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.98124 | 21.8052 | 0 | 0 | 0
8 | 1 | 9 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.44928 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.57314 | 12.7364 | 0 | 0 | 0
8 | 1 | 10 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.8293 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.19312 | 4.2916 | 0 | 0 | 0
8 | 1 | 11 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.1157 | 100 | 1.5 | 100 | 2 | 100 | 2.8917 | 96.8746 | 0 | 0 | 0 | 0 | 0
8 | 1 | 12 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.301 | 100 | 1.5 | 100 | 2 | 100 | 2.7064 | 90.666 | 0 | 0 | 0 | 0 | 0
8 | 1 | 13 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.3703 | 100 | 1.5 | 100 | 2 | 100 | 2.6371 | 88.3456 | 0 | 0 | 0 | 0 | 0
8 | 1 | 14 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.3179 | 100 | 1.5 | 100 | 2 | 100 | 2.6895 | 90.1016 | 0 | 0 | 0 | 0 | 0
8 | 1 | 15 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.155 | 100 | 1.5 | 100 | 2 | 100 | 2.8524 | 95.5576 | 0 | 0 | 0 | 0 | 0
8 | 1 | 16 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.88171 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.14071 | 3.1268 | 0 | 0 | 0
8 | 1 | 17 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.53165 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.49077 | 10.906 | 0 | 0 | 0
8 | 1 | 18 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.07488 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.94754 | 21.0564 | 0 | 0 | 0
8 | 1 | 19 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 1 | 20 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 1 | 21 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 1 | 22 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 1 | 23 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 1 | 24 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 2 | 1 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 2 | 2 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 2 | 3 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 2 | 4 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 2 | 5 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 2 | 6 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 2 | 7 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 2 | 8 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.067392 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.95503 | 21.2228 | 0 | 0 | 0
8 | 2 | 9 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.49046 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.53196 | 11.8212 | 0 | 0 | 0
8 | 2 | 10 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.87048 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.15194 | 3.3764 | 0 | 0 | 0
8 | 2 | 11 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.1681 | 100 | 1.5 | 100 | 2 | 100 | 2.8393 | 95.1187 | 0 | 0 | 0 | 0 | 0
8 | 2 | 12 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.3684 | 100 | 1.5 | 100 | 2 | 100 | 2.639 | 88.4083 | 0 | 0 | 0 | 0 | 0
8 | 2 | 13 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.4471 | 100 | 1.5 | 100 | 2 | 100 | 2.5604 | 85.7743 | 0 | 0 | 0 | 0 | 0
8 | 2 | 14 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.4096 | 100 | 1.5 | 100 | 2 | 100 | 2.5978 | 87.0286 | 0 | 0 | 0 | 0 | 0
8 | 2 | 15 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.2542 | 100 | 1.5 | 100 | 2 | 100 | 2.7532 | 92.2338 | 0 | 0 | 0 | 0 | 0
8 | 2 | 16 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.9959 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.026516 | 0.58924 | 0 | 0 | 0
8 | 2 | 17 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.64958 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.37284 | 8.2852 | 0 | 0 | 0
8 | 2 | 18 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.17035 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.85207 | 18.9348 | 0 | 0 | 0
8 | 2 | 19 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 2 | 20 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 2 | 21 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 2 | 22 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 2 | 23 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 2 | 24 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 3 | 1 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 3 | 2 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 3 | 3 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 3 | 4 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 3 | 5 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 3 | 6 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 3 | 7 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.001872 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0205 | 22.6788 | 0 | 0 | 0
8 | 3 | 8 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.15538 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.86704 | 19.2676 | 0 | 0 | 0
8 | 3 | 9 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.56347 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.45895 | 10.1988 | 0 | 0 | 0
8 | 3 | 10 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.92851 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.093908 | 2.0868 | 0 | 0 | 0
8 | 3 | 11 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.2018 | 100 | 1.5 | 100 | 2 | 100 | 2.8056 | 93.9898 | 0 | 0 | 0 | 0 | 0
8 | 3 | 12 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.3909 | 100 | 1.5 | 100 | 2 | 100 | 2.6165 | 87.6557 | 0 | 0 | 0 | 0 | 0
8 | 3 | 13 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.462 | 100 | 1.5 | 100 | 2 | 100 | 2.5454 | 85.2726 | 0 | 0 | 0 | 0 | 0
8 | 3 | 14 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.4283 | 100 | 1.5 | 100 | 2 | 100 | 2.5791 | 86.4015 | 0 | 0 | 0 | 0 | 0
8 | 3 | 15 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.2374 | 100 | 1.5 | 100 | 2 | 100 | 2.77 | 92.7982 | 0 | 0 | 0 | 0 | 0
8 | 3 | 16 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.98093 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.041492 | 0.92204 | 0 | 0 | 0
8 | 3 | 17 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.6421 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.38032 | 8.4516 | 0 | 0 | 0
8 | 3 | 18 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.24149 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.78093 | 17.354 | 0 | 0 | 0
8 | 3 | 19 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.001872 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0205 | 22.6788 | 0 | 0 | 0
8 | 3 | 20 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 3 | 21 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 3 | 22 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 3 | 23 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 3 | 24 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 4 | 1 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 4 | 2 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 4 | 3 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 4 | 4 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 4 | 5 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 4 | 6 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 4 | 7 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.02808 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.99434 | 22.0964 | 0 | 0 | 0
8 | 4 | 8 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.27144 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.75098 | 16.6884 | 0 | 0 | 0
8 | 4 | 9 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.62525 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.39717 | 8.826 | 0 | 0 | 0
8 | 4 | 10 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.95098 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.071444 | 1.5876 | 0 | 0 | 0
8 | 4 | 11 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.1962 | 100 | 1.5 | 100 | 2 | 100 | 2.8112 | 94.1779 | 0 | 0 | 0 | 0 | 0
8 | 4 | 12 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.346 | 100 | 1.5 | 100 | 2 | 100 | 2.6615 | 89.1609 | 0 | 0 | 0 | 0 | 0
8 | 4 | 13 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.3928 | 100 | 1.5 | 100 | 2 | 100 | 2.6147 | 87.593 | 0 | 0 | 0 | 0 | 0
8 | 4 | 14 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.3235 | 100 | 1.5 | 100 | 2 | 100 | 2.6839 | 89.9134 | 0 | 0 | 0 | 0 | 0
8 | 4 | 15 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.1569 | 100 | 1.5 | 100 | 2 | 100 | 2.8505 | 95.4949 | 0 | 0 | 0 | 0 | 0
8 | 4 | 16 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.89856 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.12386 | 2.7524 | 0 | 0 | 0
8 | 4 | 17 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.58781 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.43461 | 9.658 | 0 | 0 | 0
8 | 4 | 18 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.2471 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.77532 | 17.2292 | 0 | 0 | 0
8 | 4 | 19 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.01872 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0037 | 22.3044 | 0 | 0 | 0
8 | 4 | 20 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 4 | 21 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 4 | 22 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 4 | 23 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 4 | 24 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 5 | 1 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 5 | 2 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 5 | 3 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 5 | 4 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 5 | 5 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 5 | 6 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 5 | 7 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.067392 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.95503 | 21.2228 | 0 | 0 | 0
8 | 5 | 8 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.29952 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.7229 | 16.0644 | 0 | 0 | 0
8 | 5 | 9 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.61027 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.41215 | 9.1588 | 0 | 0 | 0
8 | 5 | 10 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.9023 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.12012 | 2.6692 | 0 | 0 | 0
8 | 5 | 11 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.1232 | 100 | 1.5 | 100 | 2 | 100 | 2.8842 | 96.6238 | 0 | 0 | 0 | 0 | 0
8 | 5 | 12 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.2599 | 100 | 1.5 | 100 | 2 | 100 | 2.7476 | 92.0457 | 0 | 0 | 0 | 0 | 0
8 | 5 | 13 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.2973 | 100 | 1.5 | 100 | 2 | 100 | 2.7101 | 90.7914 | 0 | 0 | 0 | 0 | 0
8 | 5 | 14 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.2318 | 100 | 1.5 | 100 | 2 | 100 | 2.7756 | 92.9864 | 0 | 0 | 0 | 0 | 0
8 | 5 | 15 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.0745 | 100 | 1.5 | 100 | 2 | 100 | 2.9329 | 98.2543 | 0 | 0 | 0 | 0 | 0
8 | 5 | 16 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.83678 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.18564 | 4.1252 | 0 | 0 | 0
8 | 5 | 17 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.54288 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.47954 | 10.6564 | 0 | 0 | 0
8 | 5 | 18 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.25085 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.77157 | 17.146 | 0 | 0 | 0
8 | 5 | 19 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.035568 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.98685 | 21.93 | 0 | 0 | 0
8 | 5 | 20 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 5 | 21 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 5 | 22 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 5 | 23 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 5 | 24 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 6 | 1 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 6 | 2 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 6 | 3 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 6 | 4 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 6 | 5 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 6 | 6 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 6 | 7 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.06552 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.9569 | 21.2644 | 0 | 0 | 0
8 | 6 | 8 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.2471 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.77532 | 17.2292 | 0 | 0 | 0
8 | 6 | 9 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.50731 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.51511 | 11.4468 | 0 | 0 | 0
8 | 6 | 10 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.77501 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.24741 | 5.498 | 0 | 0 | 0
8 | 6 | 11 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.98654 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.035876 | 0.79724 | 0 | 0 | 0
8 | 6 | 12 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.1138 | 100 | 1.5 | 100 | 2 | 100 | 2.8936 | 96.9373 | 0 | 0 | 0 | 0 | 0
8 | 6 | 13 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.1663 | 100 | 1.5 | 100 | 2 | 100 | 2.8412 | 95.1814 | 0 | 0 | 0 | 0 | 0
8 | 6 | 14 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.112 | 100 | 1.5 | 100 | 2 | 100 | 2.8955 | 97.0001 | 0 | 0 | 0 | 0 | 0
8 | 6 | 15 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.9697 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.052724 | 1.1716 | 0 | 0 | 0
8 | 6 | 16 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.76752 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.2549 | 5.6644 | 0 | 0 | 0
8 | 6 | 17 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.51293 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.50949 | 11.322 | 0 | 0 | 0
8 | 6 | 18 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.25272 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.7697 | 17.1044 | 0 | 0 | 0
8 | 6 | 19 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.052416 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.97 | 21.5556 | 0 | 0 | 0
8 | 6 | 20 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 6 | 21 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 6 | 22 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 6 | 23 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 6 | 24 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 7 | 1 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 7 | 2 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 7 | 3 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 7 | 4 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 7 | 5 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 7 | 6 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 7 | 7 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.035568 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.98685 | 21.93 | 0 | 0 | 0
8 | 7 | 8 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.18346 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.83896 | 18.6436 | 0 | 0 | 0
8 | 7 | 9 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.39874 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.62368 | 13.8596 | 0 | 0 | 0
8 | 7 | 10 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.63086 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.39156 | 8.7012 | 0 | 0 | 0
8 | 7 | 11 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.82555 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.19687 | 4.3748 | 0 | 0 | 0
8 | 7 | 12 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.96408 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.05834 | 1.2964 | 0 | 0 | 0
8 | 7 | 13 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.0146 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.0077957 | 0.17324 | 0 | 0 | 0
8 | 7 | 14 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.9828 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.03962 | 0.88044 | 0 | 0 | 0
8 | 7 | 15 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.87048 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.15194 | 3.3764 | 0 | 0 | 0
8 | 7 | 16 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.67766 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.34476 | 7.6612 | 0 | 0 | 0
8 | 7 | 17 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.4549 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.56752 | 12.6116 | 0 | 0 | 0
8 | 7 | 18 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.23213 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.79029 | 17.562 | 0 | 0 | 0
8 | 7 | 19 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.054288 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.96813 | 21.514 | 0 | 0 | 0
8 | 7 | 20 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 7 | 21 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 7 | 22 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 7 | 23 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 7 | 24 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 8 | 1 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 8 | 2 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 8 | 3 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 8 | 4 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 8 | 5 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 8 | 6 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 8 | 7 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.020592 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0018 | 22.2628 | 0 | 0 | 0
8 | 8 | 8 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.18907 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.83335 | 18.5188 | 0 | 0 | 0
8 | 8 | 9 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.4343 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.58812 | 13.0692 | 0 | 0 | 0
8 | 8 | 10 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.68702 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.3354 | 7.4532 | 0 | 0 | 0
8 | 8 | 11 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.89856 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.12386 | 2.7524 | 0 | 0 | 0
8 | 8 | 12 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.0427 | 100 | 1.5 | 100 | 2 | 100 | 2.9647 | 99.3205 | 0 | 0 | 0 | 0 | 0
8 | 8 | 13 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.1026 | 100 | 1.5 | 100 | 2 | 100 | 2.9048 | 97.3136 | 0 | 0 | 0 | 0 | 0
8 | 8 | 14 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.0502 | 100 | 1.5 | 100 | 2 | 100 | 2.9572 | 99.0696 | 0 | 0 | 0 | 0 | 0
8 | 8 | 15 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.92664 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.09578 | 2.1284 | 0 | 0 | 0
8 | 8 | 16 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.71698 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.30544 | 6.7876 | 0 | 0 | 0
8 | 8 | 17 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.468 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.55442 | 12.3204 | 0 | 0 | 0
8 | 8 | 18 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.21528 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.80714 | 17.9364 | 0 | 0 | 0
8 | 8 | 19 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.026208 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.99621 | 22.138 | 0 | 0 | 0
8 | 8 | 20 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 8 | 21 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 8 | 22 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 8 | 23 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 8 | 24 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 9 | 1 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 9 | 2 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 9 | 3 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 9 | 4 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 9 | 5 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 9 | 6 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 9 | 7 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.016848 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0056 | 22.346 | 0 | 0 | 0
8 | 9 | 8 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.24336 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.77906 | 17.3124 | 0 | 0 | 0
8 | 9 | 9 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.58032 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.4421 | 9.8244 | 0 | 0 | 0
8 | 9 | 10 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.8892 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.13322 | 2.9604 | 0 | 0 | 0
8 | 9 | 11 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.1232 | 100 | 1.5 | 100 | 2 | 100 | 2.8842 | 96.6238 | 0 | 0 | 0 | 0 | 0
8 | 9 | 12 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.2692 | 100 | 1.5 | 100 | 2 | 100 | 2.7382 | 91.7321 | 0 | 0 | 0 | 0 | 0
8 | 9 | 13 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.3123 | 100 | 1.5 | 100 | 2 | 100 | 2.6951 | 90.2897 | 0 | 0 | 0 | 0 | 0
8 | 9 | 14 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.2374 | 100 | 1.5 | 100 | 2 | 100 | 2.77 | 92.7982 | 0 | 0 | 0 | 0 | 0
8 | 9 | 15 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.0539 | 100 | 1.5 | 100 | 2 | 100 | 2.9535 | 98.9442 | 0 | 0 | 0 | 0 | 0
8 | 9 | 16 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.8087 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.21372 | 4.7492 | 0 | 0 | 0
8 | 9 | 17 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.49421 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.52821 | 11.738 | 0 | 0 | 0
8 | 9 | 18 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.16099 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.86143 | 19.1428 | 0 | 0 | 0
8 | 9 | 19 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.001872 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0205 | 22.6788 | 0 | 0 | 0
8 | 9 | 20 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 9 | 21 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 9 | 22 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 9 | 23 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 9 | 24 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 10 | 1 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 10 | 2 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 10 | 3 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 10 | 4 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 10 | 5 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 10 | 6 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 10 | 7 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 10 | 8 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.25646 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.76596 | 17.0212 | 0 | 0 | 0
8 | 10 | 9 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.68515 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.33727 | 7.4948 | 0 | 0 | 0
8 | 10 | 10 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.0146 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.0077957 | 0.17324 | 0 | 0 | 0
8 | 10 | 11 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.2524 | 100 | 1.5 | 100 | 2 | 100 | 2.7551 | 92.2965 | 0 | 0 | 0 | 0 | 0
8 | 10 | 12 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.389 | 100 | 1.5 | 100 | 2 | 100 | 2.6184 | 87.7184 | 0 | 0 | 0 | 0 | 0
8 | 10 | 13 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.4115 | 100 | 1.5 | 100 | 2 | 100 | 2.5959 | 86.9659 | 0 | 0 | 0 | 0 | 0
8 | 10 | 14 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.301 | 100 | 1.5 | 100 | 2 | 100 | 2.7064 | 90.666 | 0 | 0 | 0 | 0 | 0
8 | 10 | 15 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.0914 | 100 | 1.5 | 100 | 2 | 100 | 2.916 | 97.6899 | 0 | 0 | 0 | 0 | 0
8 | 10 | 16 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.79934 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.22308 | 4.9572 | 0 | 0 | 0
8 | 10 | 17 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.44741 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.57501 | 12.778 | 0 | 0 | 0
8 | 10 | 18 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.058032 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.96439 | 21.4308 | 0 | 0 | 0
8 | 10 | 19 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 10 | 20 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 10 | 21 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 10 | 22 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 10 | 23 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 10 | 24 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 11 | 1 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 11 | 2 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 11 | 3 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 11 | 4 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 11 | 5 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 11 | 6 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 11 | 7 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 11 | 8 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.15163 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.87079 | 19.3508 | 0 | 0 | 0
8 | 11 | 9 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.61589 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.40653 | 9.034 | 0 | 0 | 0
8 | 11 | 10 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.96408 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.05834 | 1.2964 | 0 | 0 | 0
8 | 11 | 11 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.2056 | 100 | 1.5 | 100 | 2 | 100 | 2.8019 | 93.8644 | 0 | 0 | 0 | 0 | 0
8 | 11 | 12 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.3385 | 100 | 1.5 | 100 | 2 | 100 | 2.6689 | 89.4117 | 0 | 0 | 0 | 0 | 0
8 | 11 | 13 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.3516 | 100 | 1.5 | 100 | 2 | 100 | 2.6558 | 88.9727 | 0 | 0 | 0 | 0 | 0
8 | 11 | 14 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.258 | 100 | 1.5 | 100 | 2 | 100 | 2.7494 | 92.1084 | 0 | 0 | 0 | 0 | 0
8 | 11 | 15 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.0483 | 100 | 1.5 | 100 | 2 | 100 | 2.9591 | 99.1323 | 0 | 0 | 0 | 0 | 0
8 | 11 | 16 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.75254 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.26988 | 5.9972 | 0 | 0 | 0
8 | 11 | 17 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.3276 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.69482 | 15.4404 | 0 | 0 | 0
8 | 11 | 18 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 11 | 19 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 11 | 20 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 11 | 21 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 11 | 22 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 11 | 23 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 11 | 24 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 12 | 1 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 12 | 2 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 12 | 3 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 12 | 4 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 12 | 5 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 12 | 6 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 12 | 7 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 12 | 8 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.061776 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.96064 | 21.3476 | 0 | 0 | 0
8 | 12 | 9 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.51106 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.51136 | 11.3636 | 0 | 0 | 0
8 | 12 | 10 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.87422 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.1482 | 3.2932 | 0 | 0 | 0
8 | 12 | 11 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.1344 | 100 | 1.5 | 100 | 2 | 100 | 2.873 | 96.2475 | 0 | 0 | 0 | 0 | 0
8 | 12 | 12 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.2936 | 100 | 1.5 | 100 | 2 | 100 | 2.7139 | 90.9168 | 0 | 0 | 0 | 0 | 0
8 | 12 | 13 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.3366 | 100 | 1.5 | 100 | 2 | 100 | 2.6708 | 89.4744 | 0 | 0 | 0 | 0 | 0
8 | 12 | 14 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.2561 | 100 | 1.5 | 100 | 2 | 100 | 2.7513 | 92.1711 | 0 | 0 | 0 | 0 | 0
8 | 12 | 15 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 1.0633 | 100 | 1.5 | 100 | 2 | 100 | 2.9441 | 98.6306 | 0 | 0 | 0 | 0 | 0
8 | 12 | 16 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.78437 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.23805 | 5.29 | 0 | 0 | 0
8 | 12 | 17 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.3613 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.66112 | 14.6916 | 0 | 0 | 0
8 | 12 | 18 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.003744 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0187 | 22.6372 | 0 | 0 | 0
8 | 12 | 19 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 12 | 20 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 12 | 21 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 12 | 22 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 12 | 23 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0
8 | 12 | 24 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0 | 0 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 1.0224 | 22.7204 | 0 | 0 | 0

## energy
year | month | Prod Energy Req, MWh | Cooling Energy Req, MWh | Cooling Energy Req after CHP adj., MWh | BESS Charging Energy Req, MWh | Total Energy Req, MWh | Solar Output in MWh | Remaining Energy Demand (after Renewables) MWh | PPA Potential Failures | PPA Failures mitigated | PPA Unavailability, hrs | PPA Output in MWh | Gas Generator Potential Failures | Gas Generator Failures mitigated | Gas Generator Unavailability, hrs | Gas Generator Output in MWh | Grid Potential Failures | Grid Failures mitigated | Grid Unavailability, hrs | Grid Peak Energy, MWh | Grid Off Peak Energy, MWh | Final Unserved Energy Req in MWh
1 | 1 | 1391.6667 | 202.895 | 16.3179 | 9 | 1416.9846 | 300.8736 | 1116.111 | 3 | 3 | 0 | 1116.111 | 1 | 1 | 0 | 11.01 | 3 | 3 | 0 | 0 | 0 | 0
1 | 2 | 1410.7143 | 199.92 | 34.367 | 9 | 1454.0813 | 293.632 | 1160.4493 | 3 | 3 | 0 | 1160.4493 | 1 | 1 | 0 | 11.01 | 2 | 2 | 0 | 0 | 0 | 0
1 | 3 | 1259.5238 | 442.68 | 260.0918 | 9 | 1528.6156 | 336.1888 | 1192.4268 | 2 | 2 | 0 | 1192.4268 | 1 | 1 | 0 | 7.34 | 4 | 4 | 0 | 0 | 0 | 0
1 | 4 | 1394.0476 | 428.4 | 249.5632 | 9 | 1652.6109 | 319.3248 | 1333.2861 | 3 | 3 | 0 | 1333.2861 | 0 | 0 | 0 | 11.01 | 4 | 4 | 0 | 0 | 0 | 0
1 | 5 | 1260.7143 | 442.68 | 254.6184 | 9 | 1524.3327 | 313.2736 | 1211.0591 | 2 | 2 | 0 | 1211.0591 | 0 | 0 | 0 | 7.34 | 3 | 3 | 0 | 0 | 0 | 0
1 | 6 | 1282.1429 | 428.4 | 241.5139 | 9 | 1532.6567 | 271.1136 | 1261.5431 | 2 | 2 | 0 | 1261.5431 | 0 | 0 | 0 | 7.34 | 4 | 4 | 0 | 0 | 0 | 0
1 | 7 | 1309.5238 | 442.68 | 245.2716 | 9 | 1563.7954 | 240.7584 | 1323.037 | 3 | 3 | 0 | 1323.037 | 1 | 1 | 0 | 11.01 | 4 | 4 | 0 | 0 | 0 | 0
1 | 8 | 1258.3333 | 442.68 | 247.47 | 9 | 1514.8034 | 255.6384 | 1259.165 | 2 | 2 | 0 | 1259.165 | 1 | 1 | 0 | 7.34 | 2 | 2 | 0 | 0 | 0 | 0
1 | 9 | 1352.381 | 428.4 | 246.2185 | 9 | 1607.5994 | 292.3424 | 1315.257 | 3 | 3 | 0 | 1315.257 | 1 | 1 | 0 | 11.01 | 4 | 4 | 0 | 0 | 0 | 0
1 | 10 | 1366.6667 | 442.68 | 257.848 | 9 | 1633.5147 | 318.8288 | 1314.6859 | 2 | 2 | 0 | 1314.6859 | 0 | 0 | 0 | 7.34 | 2 | 2 | 0 | 0 | 0 | 0
1 | 11 | 1279.7619 | 178.5 | 0 | 9 | 1288.7619 | 286.5888 | 1002.1731 | 2 | 2 | 0 | 1002.1731 | 0 | 0 | 0 | 7.34 | 4 | 4 | 0 | 0 | 0 | 0
1 | 12 | 1428.5714 | 184.45 | 0 | 9 | 1437.5714 | 285.1008 | 1152.4706 | 2 | 2 | 0 | 1152.4706 | 1 | 1 | 0 | 7.34 | 5 | 5 | 0 | 0 | 0 | 0
2 | 1 | 1391.6667 | 202.895 | 17.9477 | 9 | 1418.6144 | 298.4472 | 1120.1672 | 2 | 2 | 0 | 1120.1672 | 0 | 0 | 0 | 7.34 | 3 | 3 | 0 | 0 | 0 | 0
2 | 2 | 1410.7143 | 199.92 | 35.8152 | 9 | 1455.5295 | 291.264 | 1164.2655 | 1 | 1 | 0 | 1164.2655 | 1 | 1 | 0 | 3.67 | 2 | 2 | 0 | 0 | 0 | 0
2 | 3 | 1259.5238 | 442.68 | 261.6894 | 9 | 1530.2132 | 333.4776 | 1196.7356 | 2 | 2 | 0 | 1196.7356 | 1 | 1 | 0 | 7.34 | 4 | 4 | 0 | 0 | 0 | 0
2 | 4 | 1394.0476 | 428.4 | 251.1266 | 9 | 1654.1742 | 316.7496 | 1337.4246 | 2 | 2 | 0 | 1337.4246 | 0 | 0 | 0 | 7.34 | 5 | 5 | 0 | 0 | 0 | 0
2 | 5 | 1260.7143 | 442.68 | 256.2602 | 9 | 1525.9745 | 310.7472 | 1215.2273 | 3 | 3 | 0 | 1215.2273 | 1 | 1 | 0 | 11.01 | 4 | 4 | 0 | 0 | 0 | 0
2 | 6 | 1282.1429 | 428.4 | 243.402 | 9 | 1534.5449 | 268.9272 | 1265.6177 | 3 | 3 | 0 | 1265.6177 | 1 | 1 | 0 | 11.01 | 2 | 2 | 0 | 0 | 0 | 0
2 | 7 | 1309.5238 | 442.68 | 247.3676 | 9 | 1565.8914 | 238.8168 | 1327.0746 | 2 | 2 | 0 | 1327.0746 | 0 | 0 | 0 | 7.34 | 4 | 4 | 0 | 0 | 0 | 0
2 | 8 | 1258.3333 | 442.68 | 249.5483 | 9 | 1516.8816 | 253.5768 | 1263.3048 | 2 | 2 | 0 | 1263.3048 | 0 | 0 | 0 | 7.34 | 5 | 5 | 0 | 0 | 0 | 0
2 | 9 | 1352.381 | 428.4 | 247.8088 | 9 | 1609.1898 | 289.9848 | 1319.205 | 3 | 3 | 0 | 1319.205 | 1 | 1 | 0 | 11.01 | 3 | 3 | 0 | 0 | 0 | 0
2 | 10 | 1366.6667 | 442.68 | 259.4638 | 9 | 1635.1305 | 316.2576 | 1318.8729 | 2 | 2 | 0 | 1318.8729 | 0 | 0 | 0 | 7.34 | 3 | 3 | 0 | 0 | 0 | 0
2 | 11 | 1279.7619 | 178.5 | 0 | 9 | 1288.7619 | 284.2776 | 1004.4843 | 2 | 2 | 0 | 1004.4843 | 0 | 0 | 0 | 7.34 | 4 | 4 | 0 | 0 | 0 | 0
2 | 12 | 1428.5714 | 184.45 | 0 | 9 | 1437.5714 | 282.8016 | 1154.7698 | 2 | 2 | 0 | 1154.7698 | 0 | 0 | 0 | 7.34 | 4 | 4 | 0 | 0 | 0 | 0
3 | 1 | 1391.6667 | 202.895 | 0 | 9 | 1400.6667 | 296.0208 | 1104.6459 | 2 | 2 | 0 | 1104.6459 | 0 | 0 | 0 | 7.34 | 3 | 3 | 0 | 0 | 0 | 0
3 | 2 | 1410.7143 | 199.92 | 10.2294 | 9 | 1429.9437 | 288.896 | 1141.0477 | 3 | 3 | 0 | 1141.0477 | 0 | 0 | 0 | 11.01 | 3 | 3 | 0 | 0 | 0 | 0
3 | 3 | 1259.5238 | 442.68 | 234.7168 | 9 | 1503.2407 | 330.7664 | 1172.4743 | 2 | 2 | 0 | 1172.4743 | 1 | 1 | 0 | 7.34 | 4 | 4 | 0 | 0 | 0 | 0
3 | 4 | 1394.0476 | 428.4 | 226.034 | 9 | 1629.0816 | 314.1744 | 1314.9072 | 1 | 1 | 0 | 1314.9072 | 1 | 1 | 0 | 3.67 | 3 | 3 | 0 | 0 | 0 | 0
3 | 5 | 1260.7143 | 442.68 | 230.5247 | 9 | 1500.239 | 308.2208 | 1192.0182 | 2 | 2 | 0 | 1192.0182 | 0 | 0 | 0 | 7.34 | 3 | 3 | 0 | 0 | 0 | 0
3 | 6 | 1282.1429 | 428.4 | 217.3053 | 9 | 1508.4481 | 266.7408 | 1241.7073 | 2 | 2 | 0 | 1241.7073 | 1 | 1 | 0 | 7.34 | 5 | 5 | 0 | 0 | 0 | 0
3 | 7 | 1309.5238 | 442.68 | 217.3798 | 9 | 1535.9036 | 236.8752 | 1299.0284 | 2 | 2 | 0 | 1299.0284 | 0 | 0 | 0 | 7.34 | 3 | 3 | 0 | 0 | 0 | 0
3 | 8 | 1258.3333 | 442.68 | 220.0779 | 9 | 1487.4113 | 251.5152 | 1235.8961 | 1 | 1 | 0 | 1235.8961 | 0 | 0 | 0 | 3.67 | 3 | 3 | 0 | 0 | 0 | 0
3 | 9 | 1352.381 | 428.4 | 221.1248 | 9 | 1582.5057 | 287.6272 | 1294.8785 | 1 | 1 | 0 | 1294.8785 | 0 | 0 | 0 | 3.67 | 3 | 3 | 0 | 0 | 0 | 0
3 | 10 | 1366.6667 | 442.68 | 231.5616 | 9 | 1607.2283 | 313.6864 | 1293.5419 | 3 | 3 | 0 | 1293.5419 | 1 | 1 | 0 | 11.01 | 4 | 4 | 0 | 0 | 0 | 0
3 | 11 | 1279.7619 | 178.5 | 0 | 9 | 1288.7619 | 281.9664 | 1006.7955 | 2 | 2 | 0 | 1006.7955 | 1 | 1 | 0 | 7.34 | 2 | 2 | 0 | 0 | 0 | 0
3 | 12 | 1428.5714 | 184.45 | 0 | 9 | 1437.5714 | 280.5024 | 1157.069 | 2 | 2 | 0 | 1157.069 | 1 | 1 | 0 | 7.34 | 3 | 3 | 0 | 0 | 0 | 0
4 | 1 | 1391.6667 | 202.895 | 0 | 9 | 1400.6667 | 293.5944 | 1107.0723 | 1 | 1 | 0 | 1107.0723 | 0 | 0 | 0 | 3.67 | 4 | 4 | 0 | 0 | 0 | 0
4 | 2 | 1410.7143 | 199.92 | 8.664 | 9 | 1428.3783 | 286.528 | 1141.8503 | 2 | 2 | 0 | 1141.8503 | 0 | 0 | 0 | 7.34 | 5 | 5 | 0 | 0 | 0 | 0
4 | 3 | 1259.5238 | 442.68 | 232.9669 | 9 | 1501.4907 | 328.0552 | 1173.4355 | 1 | 1 | 0 | 1173.4355 | 0 | 0 | 0 | 3.67 | 4 | 4 | 0 | 0 | 0 | 0
4 | 4 | 1394.0476 | 428.4 | 224.3497 | 9 | 1627.3973 | 311.5992 | 1315.7981 | 2 | 2 | 0 | 1315.7981 | 0 | 0 | 0 | 7.34 | 5 | 5 | 0 | 0 | 0 | 0
4 | 5 | 1260.7143 | 442.68 | 228.8092 | 9 | 1498.5235 | 305.6944 | 1192.8291 | 2 | 2 | 0 | 1192.8291 | 1 | 1 | 0 | 7.34 | 4 | 4 | 0 | 0 | 0 | 0
4 | 6 | 1282.1429 | 428.4 | 215.6924 | 9 | 1506.8353 | 264.5544 | 1242.2809 | 2 | 2 | 0 | 1242.2809 | 0 | 0 | 0 | 7.34 | 5 | 5 | 0 | 0 | 0 | 0
4 | 7 | 1309.5238 | 442.68 | 215.772 | 9 | 1534.2958 | 234.9336 | 1299.3622 | 2 | 2 | 0 | 1299.3622 | 0 | 0 | 0 | 7.34 | 5 | 5 | 0 | 0 | 0 | 0
4 | 8 | 1258.3333 | 442.68 | 218.448 | 9 | 1485.7813 | 249.4536 | 1236.3277 | 2 | 2 | 0 | 1236.3277 | 1 | 1 | 0 | 7.34 | 3 | 3 | 0 | 0 | 0 | 0
4 | 9 | 1352.381 | 428.4 | 219.4806 | 9 | 1580.8616 | 285.2696 | 1295.592 | 2 | 2 | 0 | 1295.592 | 0 | 0 | 0 | 7.34 | 3 | 3 | 0 | 0 | 0 | 0
4 | 10 | 1366.6667 | 442.68 | 229.8376 | 9 | 1605.5042 | 311.1152 | 1294.389 | 2 | 2 | 0 | 1294.389 | 0 | 0 | 0 | 7.34 | 3 | 3 | 0 | 0 | 0 | 0
4 | 11 | 1279.7619 | 178.5 | 0 | 9 | 1288.7619 | 279.6552 | 1009.1067 | 2 | 2 | 0 | 1009.1067 | 0 | 0 | 0 | 7.34 | 4 | 4 | 0 | 0 | 0 | 0
4 | 12 | 1428.5714 | 184.45 | 0 | 9 | 1437.5714 | 278.2032 | 1159.3682 | 2 | 2 | 0 | 1159.3682 | 1 | 1 | 0 | 7.34 | 2 | 2 | 0 | 0 | 0 | 0
5 | 1 | 1948.3333 | 202.895 | 0 | 9 | 1957.3333 | 291.168 | 1666.1653 | 3 | 3 | 0 | 1465.98 | 0 | 0 | 0 | 215.5993 | 3 | 3 | 0 | 0 | 0 | 0
5 | 2 | 1975 | 199.92 | 0 | 9 | 1984 | 284.16 | 1699.84 | 3 | 3 | 0 | 1321.98 | 0 | 0 | 0 | 393.274 | 3 | 3 | 0 | 0 | 0 | 0
5 | 3 | 1763.3333 | 442.68 | 29.8465 | 9 | 1802.1799 | 325.344 | 1476.8359 | 2 | 2 | 0 | 1473.32 | 0 | 0 | 0 | 13.7919 | 4 | 4 | 0 | 0 | 0 | 0
5 | 4 | 1951.6667 | 428.4 | 26.8143 | 9 | 1987.4809 | 309.024 | 1678.4569 | 1 | 1 | 0 | 1432.66 | 1 | 1 | 0 | 250.9349 | 3 | 3 | 0 | 10.8477 | 52.1523 | 0
5 | 5 | 1765 | 442.68 | 24.5498 | 9 | 1798.5498 | 303.168 | 1495.3818 | 2 | 2 | 0 | 1473.32 | 0 | 0 | 0 | 32.3378 | 4 | 4 | 0 | 0 | 0 | 0
5 | 6 | 1795 | 428.4 | 19.6383 | 9 | 1823.6383 | 262.368 | 1561.2703 | 1 | 1 | 0 | 1432.66 | 0 | 0 | 0 | 133.7483 | 5 | 5 | 0 | 0 | 0 | 0
5 | 7 | 1833.3333 | 442.68 | 16.2463 | 9 | 1858.5797 | 232.992 | 1625.5877 | 3 | 3 | 0 | 1465.98 | 1 | 1 | 0 | 175.0217 | 3 | 3 | 0 | 11.3607 | 51.6393 | 0
5 | 8 | 1761.6667 | 442.68 | 18.3738 | 9 | 1789.0405 | 247.392 | 1541.6485 | 1 | 1 | 0 | 1480.66 | 0 | 0 | 0 | 66.1265 | 4 | 4 | 0 | 0 | 0 | 0
5 | 9 | 1893.3333 | 428.4 | 23.672 | 9 | 1926.0054 | 282.912 | 1643.0934 | 2 | 2 | 0 | 1425.32 | 0 | 0 | 0 | 228.0494 | 4 | 4 | 0 | 0 | 0 | 0
5 | 10 | 1913.3333 | 442.68 | 27.8278 | 9 | 1950.1611 | 308.544 | 1641.6171 | 2 | 2 | 0 | 1473.32 | 1 | 1 | 0 | 178.5731 | 2 | 2 | 0 | 11.6971 | 51.3029 | 0
5 | 11 | 1791.6667 | 178.5 | 0 | 9 | 1800.6667 | 277.344 | 1523.3227 | 1 | 1 | 0 | 1432.66 | 1 | 1 | 0 | 95.8007 | 5 | 5 | 0 | 12.4787 | 50.5213 | 0
5 | 12 | 2000 | 184.45 | 0 | 9 | 2009 | 275.904 | 1733.096 | 2 | 2 | 0 | 1473.32 | 0 | 0 | 0 | 270.052 | 4 | 4 | 0 | 0 | 0 | 0
6 | 1 | 1948.3333 | 202.895 | 0 | 9 | 1957.3333 | 288.7416 | 1668.5917 | 1 | 1 | 0 | 1480.66 | 0 | 0 | 0 | 193.0697 | 3 | 3 | 0 | 0 | 0 | 0
6 | 2 | 1975 | 199.92 | 0 | 9 | 1984 | 281.792 | 1702.208 | 3 | 3 | 0 | 1321.98 | 1 | 1 | 0 | 395.642 | 3 | 3 | 0 | 11.8221 | 51.1779 | 0
6 | 3 | 1763.3333 | 442.68 | 33.867 | 9 | 1806.2003 | 322.6328 | 1483.5675 | 2 | 2 | 0 | 1473.32 | 1 | 1 | 0 | 20.5235 | 3 | 3 | 0 | 10.9769 | 52.0231 | 0
6 | 4 | 1951.6667 | 428.4 | 30.7223 | 9 | 1991.3889 | 306.4488 | 1684.9401 | 2 | 2 | 0 | 1425.32 | 0 | 0 | 0 | 269.8961 | 4 | 4 | 0 | 0 | 0 | 0
6 | 5 | 1765 | 442.68 | 28.9233 | 9 | 1802.9233 | 300.6416 | 1502.2817 | 2 | 2 | 0 | 1473.32 | 0 | 0 | 0 | 39.2377 | 4 | 4 | 0 | 0 | 0 | 0
6 | 6 | 1795 | 428.4 | 24.3322 | 9 | 1828.3322 | 260.1816 | 1568.1506 | 3 | 3 | 0 | 1417.98 | 0 | 0 | 0 | 165.5846 | 3 | 3 | 0 | 0 | 0 | 0
6 | 7 | 1833.3333 | 442.68 | 21.6177 | 9 | 1863.9511 | 231.0504 | 1632.9007 | 2 | 2 | 0 | 1473.32 | 0 | 0 | 0 | 169.8567 | 4 | 4 | 0 | 0 | 0 | 0
6 | 8 | 1761.6667 | 442.68 | 23.2401 | 9 | 1793.9068 | 245.3304 | 1548.5764 | 3 | 3 | 0 | 1465.98 | 0 | 0 | 0 | 98.0104 | 3 | 3 | 0 | 0 | 0 | 0
6 | 9 | 1893.3333 | 428.4 | 27.9735 | 9 | 1930.3069 | 280.5544 | 1649.7525 | 2 | 2 | 0 | 1425.32 | 0 | 0 | 0 | 234.7085 | 3 | 3 | 0 | 0 | 0 | 0
6 | 10 | 1913.3333 | 442.68 | 32.2402 | 9 | 1954.5735 | 305.9728 | 1648.6007 | 2 | 2 | 0 | 1473.32 | 1 | 1 | 0 | 185.5567 | 4 | 4 | 0 | 11.6971 | 51.3029 | 0
6 | 11 | 1791.6667 | 178.5 | 0 | 9 | 1800.6667 | 275.0328 | 1525.6339 | 3 | 3 | 0 | 1417.98 | 0 | 0 | 0 | 123.0679 | 3 | 3 | 0 | 0 | 0 | 0
6 | 12 | 2000 | 184.45 | 0 | 9 | 2009 | 273.6048 | 1735.3952 | 2 | 2 | 0 | 1473.32 | 1 | 1 | 0 | 272.3512 | 3 | 3 | 0 | 12.3976 | 50.6024 | 0
7 | 1 | 1948.3333 | 202.895 | 0 | 9 | 1957.3333 | 286.3152 | 1671.0181 | 1 | 1 | 0 | 1480.66 | 0 | 0 | 0 | 195.4961 | 4 | 4 | 0 | 0 | 0 | 0
7 | 2 | 1975 | 199.92 | 0 | 9 | 1984 | 279.424 | 1704.576 | 1 | 1 | 0 | 1336.66 | 1 | 1 | 0 | 373.054 | 4 | 4 | 0 | 11.8221 | 51.1779 | 0
7 | 3 | 1763.3333 | 442.68 | 38.0437 | 9 | 1810.377 | 319.9216 | 1490.4554 | 2 | 2 | 0 | 1473.32 | 1 | 1 | 0 | 27.4114 | 2 | 2 | 0 | 10.9769 | 52.0231 | 0
7 | 4 | 1951.6667 | 428.4 | 34.9744 | 9 | 1995.6411 | 303.8736 | 1691.7675 | 3 | 3 | 0 | 1417.98 | 1 | 1 | 0 | 289.2015 | 2 | 2 | 0 | 10.8477 | 52.1523 | 0
7 | 5 | 1765 | 442.68 | 33.6707 | 9 | 1807.6707 | 298.1152 | 1509.5555 | 1 | 1 | 0 | 1480.66 | 1 | 1 | 0 | 34.0335 | 3 | 3 | 0 | 10.5437 | 52.4563 | 0
7 | 6 | 1795 | 428.4 | 29.026 | 9 | 1833.026 | 257.9952 | 1575.0308 | 1 | 1 | 0 | 1432.66 | 0 | 0 | 0 | 147.5088 | 3 | 3 | 0 | 0 | 0 | 0
7 | 7 | 1833.3333 | 442.68 | 27.2542 | 9 | 1869.5875 | 229.1088 | 1640.4787 | 1 | 1 | 0 | 1480.66 | 1 | 1 | 0 | 164.9567 | 5 | 5 | 0 | 11.3607 | 51.6393 | 0
7 | 8 | 1761.6667 | 442.68 | 28.6021 | 9 | 1799.2688 | 243.2688 | 1556 | 2 | 2 | 0 | 1473.32 | 1 | 1 | 0 | 92.956 | 2 | 2 | 0 | 11.4452 | 51.5548 | 0
7 | 9 | 1893.3333 | 428.4 | 32.6368 | 9 | 1934.9701 | 278.1968 | 1656.7733 | 3 | 3 | 0 | 1417.98 | 0 | 0 | 0 | 254.2073 | 4 | 4 | 0 | 0 | 0 | 0
7 | 10 | 1913.3333 | 442.68 | 36.6526 | 9 | 1958.9859 | 303.4016 | 1655.5843 | 2 | 2 | 0 | 1473.32 | 0 | 0 | 0 | 192.5403 | 4 | 4 | 0 | 0 | 0 | 0
7 | 11 | 1791.6667 | 178.5 | 0 | 9 | 1800.6667 | 272.7216 | 1527.9451 | 2 | 2 | 0 | 1425.32 | 1 | 1 | 0 | 112.9011 | 3 | 3 | 0 | 12.4787 | 50.5213 | 0
7 | 12 | 2000 | 184.45 | 0 | 9 | 2009 | 271.3056 | 1737.6944 | 3 | 3 | 0 | 1465.98 | 1 | 1 | 0 | 287.1284 | 3 | 3 | 0 | 12.3976 | 50.6024 | 0
8 | 1 | 1948.3333 | 202.895 | 0 | 9 | 1957.3333 | 283.8888 | 1673.4445 | 3 | 3 | 0 | 1465.98 | 1 | 1 | 0 | 222.8785 | 5 | 5 | 0 | 12.8807 | 50.1193 | 0
8 | 2 | 1975 | 199.92 | 0 | 9 | 1984 | 277.056 | 1706.944 | 2 | 2 | 0 | 1329.32 | 0 | 0 | 0 | 387.9 | 4 | 4 | 0 | 0 | 0 | 0
8 | 3 | 1763.3333 | 442.68 | 42.6812 | 9 | 1815.0146 | 317.2104 | 1497.8042 | 1 | 1 | 0 | 1480.66 | 1 | 1 | 0 | 22.2822 | 3 | 3 | 0 | 10.9769 | 52.0231 | 0
8 | 4 | 1951.6667 | 428.4 | 39.6178 | 9 | 2000.2845 | 301.2984 | 1698.9861 | 1 | 1 | 0 | 1432.66 | 1 | 1 | 0 | 271.4641 | 4 | 4 | 0 | 10.8477 | 52.1523 | 0
8 | 5 | 1765 | 442.68 | 38.4899 | 9 | 1812.4899 | 295.5888 | 1516.9011 | 3 | 3 | 0 | 1465.98 | 0 | 0 | 0 | 66.3351 | 3 | 3 | 0 | 0 | 0 | 0
8 | 6 | 1795 | 428.4 | 34.2095 | 9 | 1838.2095 | 255.8088 | 1582.4007 | 2 | 2 | 0 | 1425.32 | 0 | 0 | 0 | 167.3567 | 5 | 5 | 0 | 0 | 0 | 0
8 | 7 | 1833.3333 | 442.68 | 33.4947 | 9 | 1875.828 | 227.1672 | 1648.6608 | 2 | 2 | 0 | 1473.32 | 1 | 1 | 0 | 185.6168 | 5 | 5 | 0 | 11.3607 | 51.6393 | 0
8 | 8 | 1761.6667 | 442.68 | 34.2272 | 9 | 1804.8938 | 241.2072 | 1563.6866 | 2 | 2 | 0 | 1473.32 | 1 | 1 | 0 | 100.6426 | 5 | 5 | 0 | 11.4452 | 51.5548 | 0
8 | 9 | 1893.3333 | 428.4 | 37.3 | 9 | 1939.6333 | 275.8392 | 1663.7941 | 1 | 1 | 0 | 1432.66 | 1 | 1 | 0 | 236.2721 | 4 | 4 | 0 | 12.0703 | 50.9297 | 0
8 | 10 | 1913.3333 | 442.68 | 41.1095 | 9 | 1963.4428 | 300.8304 | 1662.6124 | 2 | 2 | 0 | 1473.32 | 0 | 0 | 0 | 199.5684 | 4 | 4 | 0 | 0 | 0 | 0
8 | 11 | 1791.6667 | 178.5 | 0 | 9 | 1800.6667 | 270.4104 | 1530.2563 | 3 | 3 | 0 | 1417.98 | 0 | 0 | 0 | 127.6903 | 2 | 2 | 0 | 0 | 0 | 0
8 | 12 | 2000 | 184.45 | 0 | 9 | 2009 | 269.0064 | 1739.9936 | 1 | 1 | 0 | 1480.66 | 1 | 1 | 0 | 264.4716 | 2 | 2 | 0 | 12.3976 | 50.6024 | 0

## capex
year | Solar CAPEX, M PKR | BESS CAPEX, M PKR | PPA CAPEX, M PKR | Gas Generator CAPEX, M PKR | Grid CAPEX, M PKR | Diesel Generator CAPEX, M PKR
0 | 80 | 0 | 0 | 25 | 5 | 0
1 | 0 | 181 | 6 | 0 | 0 | 49
2 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 191 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0

## opex
year | month | Solar Depreciation Cost, M PKR | Solar Fixed Opex, M PKR | BESS Depreciation Cost, M PKR | BESS Fixed Opex, M PKR | PPA Fixed Opex, M PKR | PPA Energy Cost, M PKR | Gas Generator Depreciation Cost, M PKR | Gas Generator Fixed Opex, M PKR | Gas Generator Var OPEX, M PKR | Fuel Charges for NG, M PKR | Grid Fixed Opex, M PKR | Grid Peak Rate Energy Cost, M PKR | Grid Offpeak Rate Energy Cost, M PKR | Diesel Generator Depreciation Cost, M PKR | Diesel Generator Fixed Opex, M PKR | Diesel Generator Var OPEX, M PKR | Fuel Charges for Diesel, M PKR | Loss due to Interruptions, M PKR | Loss due to Outage, M PKR
1 | 1 | 0.44444 | 0.385 | 1.5125 | 0.66 | 0.44 | 61.2433 | 0.17361 | 0.495 | 0.042389 | 0.34566 | 2.277 | 0 | 0 | 0.4125 | 0.165 | 0 | 0 | 0 | 0
1 | 2 | 0.44444 | 0.385 | 1.5125 | 0.66 | 0.44 | 63.3682 | 0.17361 | 0.495 | 0.042389 | 0.34566 | 2.277 | 0 | 0 | 0.4125 | 0.165 | 0 | 0 | 0 | 0
1 | 3 | 0.44444 | 0.385 | 1.5125 | 0.66 | 0.44 | 65.4226 | 0.17361 | 0.495 | 0.028259 | 0.23044 | 2.277 | 0 | 0 | 0.4125 | 0.165 | 0 | 0 | 0 | 0
1 | 4 | 0.44444 | 0.385 | 1.5125 | 0.66 | 0.44 | 70.4312 | 0.17361 | 0.495 | 0.042389 | 0.34566 | 2.277 | 0 | 0 | 0.4125 | 0.165 | 0 | 0 | 0 | 0
1 | 5 | 0.44444 | 0.385 | 1.5125 | 0.66 | 0.44 | 63.8531 | 0.17361 | 0.495 | 0.028259 | 0.23044 | 2.277 | 0 | 0 | 0.4125 | 0.165 | 0 | 0 | 0 | 0
1 | 6 | 0.44444 | 0.385 | 1.5125 | 0.66 | 0.44 | 66.6827 | 0.17361 | 0.495 | 0.028259 | 0.23044 | 2.277 | 0 | 0 | 0.4125 | 0.165 | 0 | 0 | 0 | 0
1 | 7 | 0.44444 | 0.385 | 1.5125 | 0.66 | 0.44 | 72.247 | 0.17361 | 0.495 | 0.042389 | 0.34566 | 2.277 | 0 | 0 | 0.4125 | 0.165 | 0 | 0 | 0 | 0
1 | 8 | 0.44444 | 0.385 | 1.5125 | 0.66 | 0.44 | 68.5261 | 0.17361 | 0.495 | 0.028259 | 0.23044 | 2.277 | 0 | 0 | 0.4125 | 0.165 | 0 | 0 | 0 | 0
1 | 9 | 0.44444 | 0.385 | 1.5125 | 0.66 | 0.44 | 71.8405 | 0.17361 | 0.495 | 0.042389 | 0.34566 | 2.277 | 0 | 0 | 0.4125 | 0.165 | 0 | 0 | 0 | 0
1 | 10 | 0.44444 | 0.385 | 1.5125 | 0.66 | 0.44 | 69.0759 | 0.17361 | 0.495 | 0.028259 | 0.23044 | 2.277 | 0 | 0 | 0.4125 | 0.165 | 0 | 0 | 0 | 0
1 | 11 | 0.44444 | 0.385 | 1.5125 | 0.66 | 0.44 | 53.1306 | 0.17361 | 0.495 | 0.028259 | 0.23044 | 2.277 | 0 | 0 | 0.4125 | 0.165 | 0 | 0 | 0 | 0
1 | 12 | 0.44444 | 0.385 | 1.5125 | 0.66 | 0.44 | 63.5266 | 0.17361 | 0.495 | 0.028259 | 0.23044 | 2.277 | 0 | 0 | 0.4125 | 0.165 | 0 | 0 | 0 | 0
2 | 1 | 0.44444 | 0.4235 | 1.5125 | 0.726 | 0.484 | 65.0144 | 0.17361 | 0.5445 | 0.031085 | 0.24196 | 2.5047 | 0 | 0 | 0.4125 | 0.1815 | 0 | 0 | 0 | 0
2 | 2 | 0.44444 | 0.4235 | 1.5125 | 0.726 | 0.484 | 69.9244 | 0.17361 | 0.5445 | 0.015542 | 0.12098 | 2.5047 | 0 | 0 | 0.4125 | 0.1815 | 0 | 0 | 0 | 0
2 | 3 | 0.44444 | 0.4235 | 1.5125 | 0.726 | 0.484 | 72.2125 | 0.17361 | 0.5445 | 0.031085 | 0.24196 | 2.5047 | 0 | 0 | 0.4125 | 0.1815 | 0 | 0 | 0 | 0
2 | 4 | 0.44444 | 0.4235 | 1.5125 | 0.726 | 0.484 | 77.9231 | 0.17361 | 0.5445 | 0.031085 | 0.24196 | 2.5047 | 0 | 0 | 0.4125 | 0.1815 | 0 | 0 | 0 | 0
2 | 5 | 0.44444 | 0.4235 | 1.5125 | 0.726 | 0.484 | 73.2753 | 0.17361 | 0.5445 | 0.046627 | 0.36294 | 2.5047 | 0 | 0 | 0.4125 | 0.1815 | 0 | 0 | 0 | 0
2 | 6 | 0.44444 | 0.4235 | 1.5125 | 0.726 | 0.484 | 75.7496 | 0.17361 | 0.5445 | 0.046627 | 0.36294 | 2.5047 | 0 | 0 | 0.4125 | 0.1815 | 0 | 0 | 0 | 0
2 | 7 | 0.44444 | 0.4235 | 1.5125 | 0.726 | 0.484 | 77.1173 | 0.17361 | 0.5445 | 0.031085 | 0.24196 | 2.5047 | 0 | 0 | 0.4125 | 0.1815 | 0 | 0 | 0 | 0
2 | 8 | 0.44444 | 0.4235 | 1.5125 | 0.726 | 0.484 | 73.6631 | 0.17361 | 0.5445 | 0.031085 | 0.24196 | 2.5047 | 0 | 0 | 0.4125 | 0.1815 | 0 | 0 | 0 | 0
2 | 9 | 0.44444 | 0.4235 | 1.5125 | 0.726 | 0.484 | 79.0405 | 0.17361 | 0.5445 | 0.046627 | 0.36294 | 2.5047 | 0 | 0 | 0.4125 | 0.1815 | 0 | 0 | 0 | 0
2 | 10 | 0.44444 | 0.4235 | 1.5125 | 0.726 | 0.484 | 76.435 | 0.17361 | 0.5445 | 0.031085 | 0.24196 | 2.5047 | 0 | 0 | 0.4125 | 0.1815 | 0 | 0 | 0 | 0
2 | 11 | 0.44444 | 0.4235 | 1.5125 | 0.726 | 0.484 | 58.5765 | 0.17361 | 0.5445 | 0.031085 | 0.24196 | 2.5047 | 0 | 0 | 0.4125 | 0.1815 | 0 | 0 | 0 | 0
2 | 12 | 0.44444 | 0.4235 | 1.5125 | 0.726 | 0.484 | 67.2141 | 0.17361 | 0.5445 | 0.031085 | 0.24196 | 2.5047 | 0 | 0 | 0.4125 | 0.1815 | 0 | 0 | 0 | 0
3 | 1 | 0.44444 | 0.46585 | 1.5125 | 0.7986 | 0.5324 | 70.5346 | 1.5046 | 1.3976 | 0.034193 | 0.25406 | 2.7552 | 0 | 0 | 0.4125 | 0.19965 | 0 | 0 | 0 | 0
3 | 2 | 0.44444 | 0.46585 | 1.5125 | 0.7986 | 0.5324 | 72.836 | 1.5046 | 1.3976 | 0.05129 | 0.38109 | 2.7552 | 0 | 0 | 0.4125 | 0.19965 | 0 | 0 | 0 | 0
3 | 3 | 0.44444 | 0.46585 | 1.5125 | 0.7986 | 0.5324 | 77.8999 | 1.5046 | 1.3976 | 0.034193 | 0.25406 | 2.7552 | 0 | 0 | 0.4125 | 0.19965 | 0 | 0 | 0 | 0
3 | 4 | 0.44444 | 0.46585 | 1.5125 | 0.7986 | 0.5324 | 86.6728 | 1.5046 | 1.3976 | 0.017097 | 0.12703 | 2.7552 | 0 | 0 | 0.4125 | 0.19965 | 0 | 0 | 0 | 0
3 | 5 | 0.44444 | 0.46585 | 1.5125 | 0.7986 | 0.5324 | 76.0585 | 1.5046 | 1.3976 | 0.034193 | 0.25406 | 2.7552 | 0 | 0 | 0.4125 | 0.19965 | 0 | 0 | 0 | 0
3 | 6 | 0.44444 | 0.46585 | 1.5125 | 0.7986 | 0.5324 | 82.509 | 1.5046 | 1.3976 | 0.034193 | 0.25406 | 2.7552 | 0 | 0 | 0.4125 | 0.19965 | 0 | 0 | 0 | 0
3 | 7 | 0.44444 | 0.46585 | 1.5125 | 0.7986 | 0.5324 | 82.8239 | 1.5046 | 1.3976 | 0.034193 | 0.25406 | 2.7552 | 0 | 0 | 0.4125 | 0.19965 | 0 | 0 | 0 | 0
3 | 8 | 0.44444 | 0.46585 | 1.5125 | 0.7986 | 0.5324 | 78.8325 | 1.5046 | 1.3976 | 0.017097 | 0.12703 | 2.7552 | 0 | 0 | 0.4125 | 0.19965 | 0 | 0 | 0 | 0
3 | 9 | 0.44444 | 0.46585 | 1.5125 | 0.7986 | 0.5324 | 82.5615 | 1.5046 | 1.3976 | 0.017097 | 0.12703 | 2.7552 | 0 | 0 | 0.4125 | 0.19965 | 0 | 0 | 0 | 0
3 | 10 | 0.44444 | 0.46585 | 1.5125 | 0.7986 | 0.5324 | 85.5541 | 1.5046 | 1.3976 | 0.05129 | 0.38109 | 2.7552 | 0 | 0 | 0.4125 | 0.19965 | 0 | 0 | 0 | 0
3 | 11 | 0.44444 | 0.46585 | 1.5125 | 0.7986 | 0.5324 | 66.9612 | 1.5046 | 1.3976 | 0.034193 | 0.25406 | 2.7552 | 0 | 0 | 0.4125 | 0.19965 | 0 | 0 | 0 | 0
3 | 12 | 0.44444 | 0.46585 | 1.5125 | 0.7986 | 0.5324 | 76.6939 | 1.5046 | 1.3976 | 0.034193 | 0.25406 | 2.7552 | 0 | 0 | 0.4125 | 0.19965 | 0 | 0 | 0 | 0
4 | 1 | 0.44444 | 0.51244 | 1.5125 | 0.87846 | 0.58564 | 78.012 | 1.5046 | 1.5373 | 0.018806 | 0.13338 | 3.0307 | 0 | 0 | 0.4125 | 0.21962 | 0 | 0 | 0 | 0
4 | 2 | 0.44444 | 0.51244 | 1.5125 | 0.87846 | 0.58564 | 80.6858 | 1.5046 | 1.5373 | 0.037613 | 0.26676 | 3.0307 | 0 | 0 | 0.4125 | 0.21962 | 0 | 0 | 0 | 0
4 | 3 | 0.44444 | 0.51244 | 1.5125 | 0.87846 | 0.58564 | 82.6272 | 1.5046 | 1.5373 | 0.018806 | 0.13338 | 3.0307 | 0 | 0 | 0.4125 | 0.21962 | 0 | 0 | 0 | 0
4 | 4 | 0.44444 | 0.51244 | 1.5125 | 0.87846 | 0.58564 | 92.783 | 1.5046 | 1.5373 | 0.037613 | 0.26676 | 3.0307 | 0 | 0 | 0.4125 | 0.21962 | 0 | 0 | 0 | 0
4 | 5 | 0.44444 | 0.51244 | 1.5125 | 0.87846 | 0.58564 | 87.1054 | 1.5046 | 1.5373 | 0.037613 | 0.26676 | 3.0307 | 0 | 0 | 0.4125 | 0.21962 | 0 | 0 | 0 | 0
4 | 6 | 0.44444 | 0.51244 | 1.5125 | 0.87846 | 0.58564 | 87.6703 | 1.5046 | 1.5373 | 0.037613 | 0.26676 | 3.0307 | 0 | 0 | 0.4125 | 0.21962 | 0 | 0 | 0 | 0
4 | 7 | 0.44444 | 0.51244 | 1.5125 | 0.87846 | 0.58564 | 91.64 | 1.5046 | 1.5373 | 0.037613 | 0.26676 | 3.0307 | 0 | 0 | 0.4125 | 0.21962 | 0 | 0 | 0 | 0
4 | 8 | 0.44444 | 0.51244 | 1.5125 | 0.87846 | 0.58564 | 89.8753 | 1.5046 | 1.5373 | 0.037613 | 0.26676 | 3.0307 | 0 | 0 | 0.4125 | 0.21962 | 0 | 0 | 0 | 0
4 | 9 | 0.44444 | 0.51244 | 1.5125 | 0.87846 | 0.58564 | 90.8673 | 1.5046 | 1.5373 | 0.037613 | 0.26676 | 3.0307 | 0 | 0 | 0.4125 | 0.21962 | 0 | 0 | 0 | 0
4 | 10 | 0.44444 | 0.51244 | 1.5125 | 0.87846 | 0.58564 | 90.7836 | 1.5046 | 1.5373 | 0.037613 | 0.26676 | 3.0307 | 0 | 0 | 0.4125 | 0.21962 | 0 | 0 | 0 | 0
4 | 11 | 0.44444 | 0.51244 | 1.5125 | 0.87846 | 0.58564 | 71.199 | 1.5046 | 1.5373 | 0.037613 | 0.26676 | 3.0307 | 0 | 0 | 0.4125 | 0.21962 | 0 | 0 | 0 | 0
4 | 12 | 0.44444 | 0.51244 | 1.5125 | 0.87846 | 0.58564 | 84.2679 | 1.5046 | 1.5373 | 0.037613 | 0.26676 | 3.0307 | 0 | 0 | 0.4125 | 0.21962 | 0 | 0 | 0 | 0
5 | 1 | 0.44444 | 0.56368 | 1.5125 | 0.96631 | 0.6442 | 113.3255 | 1.5046 | 1.691 | 1.2153 | 8.2274 | 3.3338 | 0 | 0 | 0.4125 | 0.24158 | 0 | 0 | 0 | 0
5 | 2 | 0.44444 | 0.56368 | 1.5125 | 0.96631 | 0.6442 | 102.3096 | 1.5046 | 1.691 | 2.2168 | 15.0077 | 3.3338 | 0 | 0 | 0.4125 | 0.24158 | 0 | 0 | 0 | 0
5 | 3 | 0.44444 | 0.56368 | 1.5125 | 0.96631 | 0.6442 | 113.4939 | 1.5046 | 1.691 | 0.13567 | 0.91845 | 3.3338 | 0 | 0 | 0.4125 | 0.24158 | 0 | 0 | 0 | 0
5 | 4 | 0.44444 | 0.56368 | 1.5125 | 0.96631 | 0.6442 | 109.9904 | 1.5046 | 1.691 | 1.4724 | 9.968 | 3.3338 | 0.90129 | 3.846 | 0.4125 | 0.24158 | 0 | 0 | 0 | 0
5 | 5 | 0.44444 | 0.56368 | 1.5125 | 0.96631 | 0.6442 | 113.4939 | 1.5046 | 1.691 | 0.2402 | 1.6262 | 3.3338 | 0 | 0 | 0.4125 | 0.24158 | 0 | 0 | 0 | 0
5 | 6 | 0.44444 | 0.56368 | 1.5125 | 0.96631 | 0.6442 | 109.9904 | 1.5046 | 1.691 | 0.86976 | 5.8882 | 3.3338 | 0 | 0 | 0.4125 | 0.24158 | 0 | 0 | 0 | 0
5 | 7 | 0.44444 | 0.56368 | 1.5125 | 0.96631 | 0.6442 | 113.3255 | 1.5046 | 1.691 | 0.98656 | 6.679 | 3.3338 | 0.94391 | 3.8082 | 0.4125 | 0.24158 | 0 | 0 | 0 | 0
5 | 8 | 0.44444 | 0.56368 | 1.5125 | 0.96631 | 0.6442 | 113.6624 | 1.5046 | 1.691 | 0.45963 | 3.1117 | 3.3338 | 0 | 0 | 0.4125 | 0.24158 | 0 | 0 | 0 | 0
5 | 9 | 0.44444 | 0.56368 | 1.5125 | 0.96631 | 0.6442 | 109.822 | 1.5046 | 1.691 | 1.3434 | 9.0947 | 3.3338 | 0 | 0 | 0.4125 | 0.24158 | 0 | 0 | 0 | 0
5 | 10 | 0.44444 | 0.56368 | 1.5125 | 0.96631 | 0.6442 | 113.4939 | 1.5046 | 1.691 | 1.0066 | 6.8145 | 3.3338 | 0.97187 | 3.7833 | 0.4125 | 0.24158 | 0 | 0 | 0 | 0
5 | 11 | 0.44444 | 0.56368 | 1.5125 | 0.96631 | 0.6442 | 109.9904 | 1.5046 | 1.691 | 0.65585 | 4.4401 | 3.3338 | 1.0368 | 3.7257 | 0.4125 | 0.24158 | 0 | 0 | 0 | 0
5 | 12 | 0.44444 | 0.56368 | 1.5125 | 0.96631 | 0.6442 | 113.4939 | 1.5046 | 1.691 | 1.5801 | 10.6975 | 3.3338 | 0 | 0 | 0.4125 | 0.24158 | 0 | 0 | 0 | 0
6 | 1 | 0.44444 | 0.62005 | 1.5125 | 1.0629 | 0.70862 | 125.0286 | 1.5046 | 1.8601 | 1.2608 | 8.1478 | 3.6671 | 0 | 0 | 0.4125 | 0.26573 | 0 | 0 | 0 | 0
6 | 2 | 0.44444 | 0.62005 | 1.5125 | 1.0629 | 0.70862 | 112.5406 | 1.5046 | 1.8601 | 2.4532 | 15.8529 | 3.6671 | 1.0805 | 4.1515 | 0.4125 | 0.26573 | 0 | 0 | 0 | 0
6 | 3 | 0.44444 | 0.62005 | 1.5125 | 1.0629 | 0.70862 | 124.8433 | 1.5046 | 1.8601 | 0.15911 | 1.0282 | 3.6671 | 1.0032 | 4.2201 | 0.4125 | 0.26573 | 0 | 0 | 0 | 0
6 | 4 | 0.44444 | 0.62005 | 1.5125 | 1.0629 | 0.70862 | 120.8042 | 1.5046 | 1.8601 | 1.7372 | 11.2262 | 3.6671 | 0 | 0 | 0.4125 | 0.26573 | 0 | 0 | 0 | 0
6 | 5 | 0.44444 | 0.62005 | 1.5125 | 1.0629 | 0.70862 | 124.8433 | 1.5046 | 1.8601 | 0.30701 | 1.984 | 3.6671 | 0 | 0 | 0.4125 | 0.26573 | 0 | 0 | 0 | 0
6 | 6 | 0.44444 | 0.62005 | 1.5125 | 1.0629 | 0.70862 | 120.6189 | 1.5046 | 1.8601 | 1.0267 | 6.6348 | 3.6671 | 0 | 0 | 0.4125 | 0.26573 | 0 | 0 | 0 | 0
6 | 7 | 0.44444 | 0.62005 | 1.5125 | 1.0629 | 0.70862 | 124.8433 | 1.5046 | 1.8601 | 1.1169 | 7.2177 | 3.6671 | 0 | 0 | 0.4125 | 0.26573 | 0 | 0 | 0 | 0
6 | 8 | 0.44444 | 0.62005 | 1.5125 | 1.0629 | 0.70862 | 124.658 | 1.5046 | 1.8601 | 0.60771 | 3.9272 | 3.6671 | 0 | 0 | 0.4125 | 0.26573 | 0 | 0 | 0 | 0
6 | 9 | 0.44444 | 0.62005 | 1.5125 | 1.0629 | 0.70862 | 120.8042 | 1.5046 | 1.8601 | 1.4872 | 9.6104 | 3.6671 | 0 | 0 | 0.4125 | 0.26573 | 0 | 0 | 0 | 0
6 | 10 | 0.44444 | 0.62005 | 1.5125 | 1.0629 | 0.70862 | 124.8433 | 1.5046 | 1.8601 | 1.2143 | 7.8468 | 3.6671 | 1.0691 | 4.1617 | 0.4125 | 0.26573 | 0 | 0 | 0 | 0
6 | 11 | 0.44444 | 0.62005 | 1.5125 | 1.0629 | 0.70862 | 120.6189 | 1.5046 | 1.8601 | 0.76308 | 4.9312 | 3.6671 | 0 | 0 | 0.4125 | 0.26573 | 0 | 0 | 0 | 0
6 | 12 | 0.44444 | 0.62005 | 1.5125 | 1.0629 | 0.70862 | 124.8433 | 1.5046 | 1.8601 | 1.7206 | 11.1187 | 3.6671 | 1.1331 | 4.1049 | 0.4125 | 0.26573 | 0 | 0 | 0 | 0
7 | 1 | 0.44444 | 0.68205 | 1.5125 | 1.1692 | 0.77949 | 137.5315 | 1.5046 | 2.0462 | 1.4385 | 8.8735 | 4.0338 | 0 | 0 | 0.4125 | 0.29231 | 0 | 0 | 0 | 0
7 | 2 | 0.44444 | 0.68205 | 1.5125 | 1.1692 | 0.77949 | 124.2023 | 1.5046 | 2.0462 | 2.6495 | 16.3437 | 4.0338 | 1.1885 | 4.5667 | 0.4125 | 0.29231 | 0 | 0 | 0 | 0
7 | 3 | 0.44444 | 0.68205 | 1.5125 | 1.1692 | 0.77949 | 137.3277 | 1.5046 | 2.0462 | 0.18696 | 1.1533 | 4.0338 | 1.1036 | 4.6421 | 0.4125 | 0.29231 | 0 | 0 | 0 | 0
7 | 4 | 0.44444 | 0.68205 | 1.5125 | 1.1692 | 0.77949 | 132.2052 | 1.5046 | 2.0462 | 1.9725 | 12.1674 | 4.0338 | 1.0906 | 4.6536 | 0.4125 | 0.29231 | 0 | 0 | 0 | 0
7 | 5 | 0.44444 | 0.68205 | 1.5125 | 1.1692 | 0.77949 | 137.5315 | 1.5046 | 2.0462 | 0.30221 | 1.8642 | 4.0338 | 1.06 | 4.6808 | 0.4125 | 0.29231 | 0 | 0 | 0 | 0
7 | 6 | 0.44444 | 0.68205 | 1.5125 | 1.1692 | 0.77949 | 133.0884 | 1.5046 | 2.0462 | 1.0762 | 6.6384 | 4.0338 | 0 | 0 | 0.4125 | 0.29231 | 0 | 0 | 0 | 0
7 | 7 | 0.44444 | 0.68205 | 1.5125 | 1.1692 | 0.77949 | 137.5315 | 1.5046 | 2.0462 | 1.2653 | 7.8048 | 4.0338 | 1.1421 | 4.6079 | 0.4125 | 0.29231 | 0 | 0 | 0 | 0
7 | 8 | 0.44444 | 0.68205 | 1.5125 | 1.1692 | 0.77949 | 137.3277 | 1.5046 | 2.0462 | 0.63401 | 3.9109 | 4.0338 | 1.1506 | 4.6003 | 0.4125 | 0.29231 | 0 | 0 | 0 | 0
7 | 9 | 0.44444 | 0.68205 | 1.5125 | 1.1692 | 0.77949 | 133.1564 | 1.5046 | 2.0462 | 1.7338 | 10.6951 | 4.0338 | 0 | 0 | 0.4125 | 0.29231 | 0 | 0 | 0 | 0
7 | 10 | 0.44444 | 0.68205 | 1.5125 | 1.1692 | 0.77949 | 137.3277 | 1.5046 | 2.0462 | 1.3833 | 8.5329 | 4.0338 | 0 | 0 | 0.4125 | 0.29231 | 0 | 0 | 0 | 0
7 | 11 | 0.44444 | 0.68205 | 1.5125 | 1.1692 | 0.77949 | 132.8846 | 1.5046 | 2.0462 | 0.80509 | 4.9662 | 4.0338 | 1.2545 | 4.5081 | 0.4125 | 0.29231 | 0 | 0 | 0 | 0
7 | 12 | 0.44444 | 0.68205 | 1.5125 | 1.1692 | 0.77949 | 137.1238 | 1.5046 | 2.0462 | 1.9584 | 12.0802 | 4.0338 | 1.2464 | 4.5153 | 0.4125 | 0.29231 | 0 | 0 | 0 | 0
8 | 1 | 0.44444 | 0.75026 | 1.5125 | 1.2862 | 0.85744 | 151.3594 | 1.5046 | 2.2508 | 1.7107 | 10.0728 | 4.4372 | 1.4244 | 4.9195 | 0.4125 | 0.32154 | 0 | 0 | 0 | 0
8 | 2 | 0.44444 | 0.75026 | 1.5125 | 1.2862 | 0.85744 | 136.3983 | 1.5046 | 2.2508 | 2.9873 | 17.5898 | 4.4372 | 0 | 0 | 0.4125 | 0.32154 | 0 | 0 | 0 | 0
8 | 3 | 0.44444 | 0.75026 | 1.5125 | 1.2862 | 0.85744 | 151.2846 | 1.5046 | 2.2508 | 0.24427 | 1.4383 | 4.4372 | 1.2139 | 5.1063 | 0.4125 | 0.32154 | 0 | 0 | 0 | 0
8 | 4 | 0.44444 | 0.75026 | 1.5125 | 1.2862 | 0.85744 | 146.3973 | 1.5046 | 2.2508 | 2.1523 | 12.6731 | 4.4372 | 1.1996 | 5.119 | 0.4125 | 0.32154 | 0 | 0 | 0 | 0
8 | 5 | 0.44444 | 0.75026 | 1.5125 | 1.2862 | 0.85744 | 150.8362 | 1.5046 | 2.2508 | 0.49768 | 2.9304 | 4.4372 | 0 | 0 | 0.4125 | 0.32154 | 0 | 0 | 0 | 0
8 | 6 | 0.44444 | 0.75026 | 1.5125 | 1.2862 | 0.85744 | 146.1731 | 1.5046 | 2.2508 | 1.3712 | 8.0741 | 4.4372 | 0 | 0 | 0.4125 | 0.32154 | 0 | 0 | 0 | 0
8 | 7 | 0.44444 | 0.75026 | 1.5125 | 1.2862 | 0.85744 | 151.0604 | 1.5046 | 2.2508 | 1.5082 | 8.8807 | 4.4372 | 1.2563 | 5.0687 | 0.4125 | 0.32154 | 0 | 0 | 0 | 0
8 | 8 | 0.44444 | 0.75026 | 1.5125 | 1.2862 | 0.85744 | 151.0604 | 1.5046 | 2.2508 | 0.87072 | 5.1269 | 4.4372 | 1.2657 | 5.0604 | 0.4125 | 0.32154 | 0 | 0 | 0 | 0
8 | 9 | 0.44444 | 0.75026 | 1.5125 | 1.2862 | 0.85744 | 146.3973 | 1.5046 | 2.2508 | 1.8883 | 11.1185 | 4.4372 | 1.3348 | 4.999 | 0.4125 | 0.32154 | 0 | 0 | 0 | 0
8 | 10 | 0.44444 | 0.75026 | 1.5125 | 1.2862 | 0.85744 | 151.0604 | 1.5046 | 2.2508 | 1.5744 | 9.2701 | 4.4372 | 0 | 0 | 0.4125 | 0.32154 | 0 | 0 | 0 | 0
8 | 11 | 0.44444 | 0.75026 | 1.5125 | 1.2862 | 0.85744 | 145.4257 | 1.5046 | 2.2508 | 0.958 | 5.6408 | 4.4372 | 0 | 0 | 0.4125 | 0.32154 | 0 | 0 | 0 | 0
8 | 12 | 0.44444 | 0.75026 | 1.5125 | 1.2862 | 0.85744 | 151.2846 | 1.5046 | 2.2508 | 2.0228 | 11.9103 | 4.4372 | 1.371 | 4.9669 | 0.4125 | 0.32154 | 0 | 0 | 0 | 0

## emissions
year | month | CO2 Emissions from PPA, MT | CO2 Emissions from Gas Generator, MT | CO2 Emissions from Grid, MT | CO2 Emissions from Diesel Generator, MT
1 | 1 | 410.2423 | 2.202 | 0 | 0
1 | 2 | 424.4762 | 2.202 | 0 | 0
1 | 3 | 438.2374 | 1.468 | 0 | 0
1 | 4 | 471.7881 | 2.202 | 0 | 0
1 | 5 | 427.7242 | 1.468 | 0 | 0
1 | 6 | 446.6781 | 1.468 | 0 | 0
1 | 7 | 483.951 | 2.202 | 0 | 0
1 | 8 | 459.0267 | 1.468 | 0 | 0
1 | 9 | 481.228 | 2.202 | 0 | 0
1 | 10 | 462.7091 | 1.468 | 0 | 0
1 | 11 | 355.8986 | 1.468 | 0 | 0
1 | 12 | 425.5372 | 1.468 | 0 | 0
2 | 1 | 395.912 | 1.468 | 0 | 0
2 | 2 | 425.8119 | 0.734 | 0 | 0
2 | 3 | 439.7455 | 1.468 | 0 | 0
2 | 4 | 474.5211 | 1.468 | 0 | 0
2 | 5 | 446.2176 | 2.202 | 0 | 0
2 | 6 | 461.2852 | 2.202 | 0 | 0
2 | 7 | 469.6141 | 1.468 | 0 | 0
2 | 8 | 448.5792 | 1.468 | 0 | 0
2 | 9 | 481.3252 | 2.202 | 0 | 0
2 | 10 | 465.459 | 1.468 | 0 | 0
2 | 11 | 356.7075 | 1.468 | 0 | 0
2 | 12 | 409.3074 | 1.468 | 0 | 0
3 | 1 | 390.4796 | 1.468 | 0 | 0
3 | 2 | 403.2202 | 2.202 | 0 | 0
3 | 3 | 431.254 | 1.468 | 0 | 0
3 | 4 | 479.821 | 0.734 | 0 | 0
3 | 5 | 421.0599 | 1.468 | 0 | 0
3 | 6 | 456.7701 | 1.468 | 0 | 0
3 | 7 | 458.5134 | 1.468 | 0 | 0
3 | 8 | 436.4171 | 0.734 | 0 | 0
3 | 9 | 457.061 | 0.734 | 0 | 0
3 | 10 | 473.6277 | 2.202 | 0 | 0
3 | 11 | 370.6974 | 1.468 | 0 | 0
3 | 12 | 424.5777 | 1.468 | 0 | 0
4 | 1 | 392.6133 | 0.734 | 0 | 0
4 | 2 | 406.0701 | 1.468 | 0 | 0
4 | 3 | 415.8404 | 0.734 | 0 | 0
4 | 4 | 466.9518 | 1.468 | 0 | 0
4 | 5 | 438.3782 | 1.468 | 0 | 0
4 | 6 | 441.2208 | 1.468 | 0 | 0
4 | 7 | 461.1993 | 1.468 | 0 | 0
4 | 8 | 452.3182 | 1.468 | 0 | 0
4 | 9 | 457.3107 | 1.468 | 0 | 0
4 | 10 | 456.8897 | 1.468 | 0 | 0
4 | 11 | 358.3253 | 1.468 | 0 | 0
4 | 12 | 424.0979 | 1.468 | 0 | 0
5 | 1 | 518.4879 | 43.1199 | 0 | 0
5 | 2 | 468.0879 | 78.6548 | 0 | 0
5 | 3 | 519.2586 | 4.8136 | 0 | 0
5 | 4 | 503.2293 | 52.2422 | 22.05 | 0
5 | 5 | 519.2586 | 8.5228 | 0 | 0
5 | 6 | 503.2293 | 30.8601 | 0 | 0
5 | 7 | 518.4879 | 35.0043 | 22.05 | 0
5 | 8 | 520.0293 | 16.3081 | 0 | 0
5 | 9 | 502.4586 | 47.6651 | 0 | 0
5 | 10 | 519.2586 | 35.7146 | 22.05 | 0
5 | 11 | 503.2293 | 23.2705 | 22.05 | 0
5 | 12 | 519.2586 | 56.0656 | 0 | 0
6 | 1 | 520.0293 | 40.6691 | 0 | 0
6 | 2 | 468.0879 | 79.1284 | 22.05 | 0
6 | 3 | 519.2586 | 5.1323 | 22.05 | 0
6 | 4 | 502.4586 | 56.0344 | 0 | 0
6 | 5 | 519.2586 | 9.9027 | 0 | 0
6 | 6 | 501.6879 | 33.1169 | 0 | 0
6 | 7 | 519.2586 | 36.0265 | 0 | 0
6 | 8 | 518.4879 | 19.6021 | 0 | 0
6 | 9 | 502.4586 | 47.9693 | 0 | 0
6 | 10 | 519.2586 | 39.1665 | 22.05 | 0
6 | 11 | 501.6879 | 24.6136 | 0 | 0
6 | 12 | 519.2586 | 55.4978 | 22.05 | 0
7 | 1 | 520.0293 | 42.182 | 0 | 0
7 | 2 | 469.6293 | 77.6936 | 22.05 | 0
7 | 3 | 519.2586 | 5.4823 | 22.05 | 0
7 | 4 | 499.8896 | 57.8403 | 22.05 | 0
7 | 5 | 520.0293 | 8.8619 | 22.05 | 0
7 | 6 | 503.2293 | 31.557 | 0 | 0
7 | 7 | 520.0293 | 37.1017 | 22.05 | 0
7 | 8 | 519.2586 | 18.5912 | 22.05 | 0
7 | 9 | 503.4862 | 50.8415 | 0 | 0
7 | 10 | 519.2586 | 40.5633 | 0 | 0
7 | 11 | 502.4586 | 23.6078 | 22.05 | 0
7 | 12 | 518.4879 | 57.4257 | 22.05 | 0
8 | 1 | 520.2862 | 45.6033 | 22.05 | 0
8 | 2 | 468.8586 | 79.6352 | 0 | 0
8 | 3 | 520.0293 | 6.5116 | 22.05 | 0
8 | 4 | 503.2293 | 57.3756 | 22.05 | 0
8 | 5 | 518.4879 | 13.267 | 0 | 0
8 | 6 | 502.4586 | 36.5541 | 0 | 0
8 | 7 | 519.2586 | 40.2062 | 22.05 | 0
8 | 8 | 519.2586 | 23.2113 | 22.05 | 0
8 | 9 | 503.2293 | 50.3372 | 22.05 | 0
8 | 10 | 519.2586 | 41.9689 | 0 | 0
8 | 11 | 499.8896 | 25.5381 | 0 | 0
8 | 12 | 520.0293 | 53.9219 | 22.05 | 0

## summary
year | Power Fulfilment Factor, % | Energy Fulfillment Factor, % | Energy Production, MWh | OPEX, M PKR | CO2 Emissions, MT | Equivalent Tariff, PKR/kWh
1 | 100 | 100 | 18155.328 | 876.6795 | 5308.7829 | 48.2877
2 | 100 | 100 | 18172.4774 | 958.5826 | 5293.5698 | 52.7491
3 | 100 | 100 | 17911.002 | 1063.532 | 5220.381 | 59.3787
4 | 100 | 100 | 17896.068 | 1158.5234 | 5187.3637 | 64.7362
5 | 100 | 100 | 22686.6355 | 1585.8402 | 6634.7154 | 69.902
6 | 100 | 100 | 22722.5829 | 1738.2976 | 6646.2509 | 76.5009
7 | 100 | 100 | 22760.5271 | 1928.2111 | 6743.1928 | 84.7173
8 | 100 | 100 | 22800.7964 | 2110.8843 | 6742.7544 | 92.5794

## power_summary
year | month | hour | Prod Demand in MW | Cooling demand in TR | Free Cooling available in TR | BESS Charging Demand | Total power demand incl. Cooling & BESS in MW | Solar Output in MW | Solar Loading in % | BESS Output in MW | BESS Loading in % | PPA Output in MW | PPA Loading in % | Gas Generator Output in MW | Gas Generator Loading in % | Grid Output in MW | Grid Loading in % | Diesel Generator Output in MW | Diesel Generator Loading in % | Final Unserved Load
1 | 12 | 16 | 5 | 900 | 359.0325 | 0.375 | 5.7852 | 0.8313 | 100 | 1.5 | 100 | 2 | 100 | 1.4539 | 98.4012 | 0 | 0 | 0 | 0 | 0
2 | 7 | 19 | 5 | 900 | 353.565 | 0.375 | 5.7893 | 0.057072 | 100 | 1.5 | 100 | 2 | 100 | 1.455 | 100 | 0.77725 | 17.2722 | 0 | 0 | 0
3 | 4 | 7 | 5 | 900 | 785.4975 | 0.375 | 5.4618 | 0.02928 | 100 | 1.5 | 100 | 2 | 100 | 1.9325 | 59.7846 | 0 | 0 | 0 | 0 | 0
4 | 7 | 10 | 5 | 900 | 773.469 | 0.375 | 5.4709 | 0.65243 | 100 | 1.5 | 100 | 2 | 100 | 1.3185 | 41.4234 | 0 | 0 | 0 | 0 | 0
5 | 4 | 1 | 7 | 900 | 761.4405 | 0.375 | 7.4801 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.1335 | 100 | 0.84656 | 18.8124 | 0 | 0 | 0
6 | 8 | 1 | 7 | 900 | 749.412 | 0.375 | 7.4892 | 0 | 0 | 1.5 | 100 | 2 | 100 | 3.084 | 100 | 0.90518 | 20.1151 | 0 | 0 | 0
7 | 9 | 19 | 7 | 900 | 737.3835 | 0.375 | 7.4983 | 0.001888 | 100 | 1.5 | 100 | 2 | 100 | 3.0345 | 100 | 0.96191 | 21.3758 | 0 | 0 | 0
8 | 1 | 16 | 7 | 900 | 725.355 | 0.375 | 7.5074 | 0.88171 | 100 | 1.5 | 100 | 2 | 100 | 2.985 | 100 | 0.14071 | 3.1268 | 0 | 0 | 0

## energy_summary
year | Prod Energy Req, MWh | Cooling Energy Req, MWh | Cooling Energy Req after CHP adj., MWh | BESS Charging Energy Req, MWh | Total Energy Req, MWh | Solar Output in MWh | Remaining Energy Demand (after Renewables) MWh | PPA Potential Failures | PPA Failures mitigated | PPA Unavailability, hrs | PPA Output in MWh | Gas Generator Potential Failures | Gas Generator Failures mitigated | Gas Generator Unavailability, hrs | Gas Generator Output in MWh | Grid Potential Failures | Grid Failures mitigated | Grid Unavailability, hrs | Grid Peak Energy, MWh | Grid Off Peak Energy, MWh | Final Unserved Energy Req in MWh
1 | 15994.0476 | 4264.365 | 2053.2803 | 108 | 18155.328 | 3513.664 | 14641.664 | 29 | 29 | 0 | 14641.664 | 7 | 7 | 0 | 106.43 | 41 | 41 | 0 | 0 | 0 | 0
2 | 15994.0476 | 4264.365 | 2070.4298 | 108 | 18172.4774 | 3485.328 | 14687.1494 | 26 | 26 | 0 | 14687.1494 | 5 | 5 | 0 | 95.42 | 43 | 43 | 0 | 0 | 0 | 0
3 | 15994.0476 | 4264.365 | 1808.9543 | 108 | 17911.002 | 3456.992 | 14454.01 | 23 | 23 | 0 | 14454.01 | 6 | 6 | 0 | 84.41 | 39 | 39 | 0 | 0 | 0 | 0
4 | 15994.0476 | 4264.365 | 1794.0204 | 108 | 17896.068 | 3428.656 | 14467.412 | 22 | 22 | 0 | 14467.412 | 3 | 3 | 0 | 80.74 | 47 | 47 | 0 | 0 | 0 | 0
5 | 22391.6667 | 4264.365 | 186.9689 | 108 | 22686.6355 | 3400.32 | 19286.3155 | 23 | 23 | 0 | 17351.18 | 4 | 4 | 0 | 2053.3095 | 44 | 44 | 0 | 46.3842 | 205.6158 | 0
6 | 22391.6667 | 4264.365 | 222.9163 | 108 | 22722.5829 | 3371.984 | 19350.5989 | 27 | 27 | 0 | 17321.82 | 4 | 4 | 0 | 2167.5049 | 40 | 40 | 0 | 46.8936 | 205.1064 | 0
7 | 22391.6667 | 4264.365 | 260.8604 | 108 | 22760.5271 | 3343.648 | 19416.8791 | 22 | 22 | 0 | 17358.52 | 8 | 8 | 0 | 2171.3951 | 39 | 39 | 0 | 91.8725 | 412.1275 | 0
8 | 22391.6667 | 4264.365 | 301.1298 | 108 | 22800.7964 | 3315.312 | 19485.4844 | 23 | 23 | 0 | 17351.18 | 7 | 7 | 0 | 2252.4784 | 46 | 46 | 0 | 81.979 | 359.021 | 0

## energy_summary_concise
year | Total Energy Req, MWh | Solar Output in MWh | PPA Output in MWh | Gas Generator Output in MWh | Grid Peak Energy, MWh | Grid Off Peak Energy, MWh | Final Unserved Energy Req in MWh
1 | 18155.328 | 3513.664 | 14641.664 | 106.43 | 0 | 0 | 0
2 | 18172.4774 | 3485.328 | 14687.1494 | 95.42 | 0 | 0 | 0
3 | 17911.002 | 3456.992 | 14454.01 | 84.41 | 0 | 0 | 0
4 | 17896.068 | 3428.656 | 14467.412 | 80.74 | 0 | 0 | 0
5 | 22686.6355 | 3400.32 | 17351.18 | 2053.3095 | 46.3842 | 205.6158 | 0
6 | 22722.5829 | 3371.984 | 17321.82 | 2167.5049 | 46.8936 | 205.1064 | 0
7 | 22760.5271 | 3343.648 | 17358.52 | 2171.3951 | 91.8725 | 412.1275 | 0
8 | 22800.7964 | 3315.312 | 17351.18 | 2252.4784 | 81.979 | 359.021 | 0

## emissions_summary
year | CO2 Emissions from PPA, MT | CO2 Emissions from Gas Generator, MT | CO2 Emissions from Grid, MT | CO2 Emissions from Diesel Generator, MT
1 | 5287.4969 | 21.286 | 0 | 0
2 | 5274.4858 | 19.084 | 0 | 0
3 | 5203.499 | 16.882 | 0 | 0
4 | 5171.2157 | 16.148 | 0 | 0
5 | 6114.2739 | 432.2415 | 88.2 | 0
6 | 6111.1911 | 446.8598 | 88.2 | 0
7 | 6115.0446 | 451.7482 | 176.4 | 0
8 | 6114.2739 | 474.1305 | 154.35 | 0

## opex_summary
year | Solar Depreciation Cost, M PKR | Solar Fixed Opex, M PKR | BESS Depreciation Cost, M PKR | BESS Fixed Opex, M PKR | PPA Fixed Opex, M PKR | PPA Energy Cost, M PKR | Gas Generator Depreciation Cost, M PKR | Gas Generator Fixed Opex, M PKR | Gas Generator Var OPEX, M PKR | Fuel Charges for NG, M PKR | Grid Fixed Opex, M PKR | Grid Peak Rate Energy Cost, M PKR | Grid Offpeak Rate Energy Cost, M PKR | Diesel Generator Depreciation Cost, M PKR | Diesel Generator Fixed Opex, M PKR | Diesel Generator Var OPEX, M PKR | Fuel Charges for Diesel, M PKR | Loss due to Interruptions, M PKR | Loss due to Outage, M PKR
1 | 5.3333 | 4.62 | 18.15 | 7.92 | 5.28 | 789.3477 | 2.0833 | 5.94 | 0.40976 | 3.3414 | 27.324 | 0 | 0 | 4.95 | 1.98 | 0 | 0 | 0 | 0
2 | 5.3333 | 5.082 | 18.15 | 8.712 | 5.808 | 866.1459 | 2.0833 | 6.534 | 0.4041 | 3.1455 | 30.0564 | 0 | 0 | 4.95 | 2.178 | 0 | 0 | 0 | 0
3 | 5.3333 | 5.5902 | 18.15 | 9.5832 | 6.3888 | 939.9378 | 18.0553 | 16.7706 | 0.39322 | 2.9217 | 33.062 | 0 | 0 | 4.95 | 2.3958 | 0 | 0 | 0 | 0
4 | 5.3333 | 6.1492 | 18.15 | 10.5415 | 7.0277 | 1027.5169 | 18.0553 | 18.4477 | 0.41374 | 2.9344 | 36.3682 | 0 | 0 | 4.95 | 2.6354 | 0 | 0 | 0 | 0
5 | 5.3333 | 6.7641 | 18.15 | 11.5957 | 7.7304 | 1336.392 | 18.0553 | 20.2924 | 12.1823 | 82.4734 | 40.0051 | 3.8539 | 15.1632 | 4.95 | 2.8989 | 0 | 0 | 0 | 0
6 | 5.3333 | 7.4406 | 18.15 | 12.7552 | 8.5035 | 1469.2901 | 18.0553 | 22.3217 | 13.8537 | 89.5258 | 44.0056 | 4.2858 | 16.6382 | 4.95 | 3.1888 | 0 | 0 | 0 | 0
7 | 5.3333 | 8.1846 | 18.15 | 14.0308 | 9.3538 | 1617.2382 | 18.0553 | 24.5538 | 15.4058 | 95.0304 | 48.4061 | 9.2363 | 36.7749 | 4.95 | 3.5077 | 0 | 0 | 0 | 0
8 | 5.3333 | 9.0031 | 18.15 | 15.4338 | 10.2892 | 1778.7378 | 18.0553 | 27.0092 | 17.786 | 104.7257 | 53.2467 | 9.0659 | 35.2397 | 4.95 | 3.8585 | 0 | 0 | 0 | 0

## opex_summary_concise
year | BESS Fixed Opex, M PKR | Gas Generator Fixed Opex, M PKR | Fuel Charges for NG, M PKR | Loss due to Interruptions, M PKR | Loss due to Outage, M PKR | Source Depreciation, M PKR | Renewable OPEX, M PKR | Power Plant OPEX, M PKR | Diesel OPEX, M PKR | Grid OPEX, M PKR | PPA OPEX, M PKR
1 | 7.92 | 5.94 | 3.3414 | 0 | 0 | 30.5167 | 4.62 | 0.40976 | 1.98 | 27.324 | 794.6277
2 | 8.712 | 6.534 | 3.1455 | 0 | 0 | 30.5167 | 5.082 | 0.4041 | 2.178 | 30.0564 | 871.9539
3 | 9.5832 | 16.7706 | 2.9217 | 0 | 0 | 46.4887 | 5.5902 | 0.39322 | 2.3958 | 33.062 | 946.3266
4 | 10.5415 | 18.4477 | 2.9344 | 0 | 0 | 46.4887 | 6.1492 | 0.41374 | 2.6354 | 36.3682 | 1034.5445
5 | 11.5957 | 20.2924 | 82.4734 | 0 | 0 | 46.4887 | 6.7641 | 12.1823 | 2.8989 | 59.0221 | 1344.1225
6 | 12.7552 | 22.3217 | 89.5258 | 0 | 0 | 46.4887 | 7.4406 | 13.8537 | 3.1888 | 64.9296 | 1477.7936
7 | 14.0308 | 24.5538 | 95.0304 | 0 | 0 | 46.4887 | 8.1846 | 15.4058 | 3.5077 | 94.4173 | 1626.592
8 | 15.4338 | 27.0092 | 104.7257 | 0 | 0 | 46.4887 | 9.0031 | 17.786 | 3.8585 | 97.5523 | 1789.027