## wind
Capital Cost baseline | OPEX baseline | Useful Life | Fixed OPEX inflation rate | Days of year | Hours of day | Power Density at Site | Wind Class applicable as IEC standards | Selected Turbine's rotor diameter | Swept Area | Tower Height | Power Density of Turbine | Avg Speed (based on location) | Turbine Rated power | Wind turbine Output multiplier 1 | Wind turbine Output multiplier 2 | Wind turbine Output multiplier 3 | Wind turbine space required for 2MW | Fail/ year | Down-time (hrs) | Degradation
280000000 | 388888 | 15 | 0.1 | 365 | 24 | 428 |  | 122 | 11690 | 108 | 188.19 | 7.8 | 2.2 | 0.46 | 0.74 | 0.98 | 6100 | 1 | 72 | 1.5
per MW | per MW per month
Month | Per Month Energy Output | Output Prop
1 | 0.84 | 0.07
2 | 0.92 | 0.076667
3 | 0.93 | 0.0775
4 | 1.08 | 0.09
5 | 1.28 | 0.10667
6 | 1.2 | 0.1
7 | 1.18 | 0.098333
8 | 1.07 | 0.089167
9 | 1.02 | 0.085
10 | 0.82 | 0.068333
11 | 0.8 | 0.066667
12 | 0.86 | 0.071667
Month | Average Day Time (hours) | Windspeed at 100m
1 | 1 | 7.0064
1 | 2 | 7.2145
1 | 3 | 7.3533
1 | 4 | 7.2145
1 | 5 | 6.4514
1 | 6 | 5.5496
1 | 7 | 5.2028
1 | 8 | 4.9947
1 | 9 | 4.7866
1 | 10 | 4.6478
1 | 11 | 4.5091
1 | 12 | 4.5091
1 | 13 | 4.7172
1 | 14 | 5.3415
1 | 15 | 5.619
1 | 16 | 5.619
1 | 17 | 5.4803
1 | 18 | 5.5496
1 | 19 | 5.619
1 | 20 | 5.8271
1 | 21 | 6.174
1 | 22 | 6.5208
1 | 23 | 6.7289
1 | 24 | 6.8677
2 | 1 | 7.0163
2 | 2 | 7.1352
2 | 3 | 6.9569
2 | 4 | 6.5406
2 | 5 | 5.4704
2 | 6 | 4.6974
2 | 7 | 4.3406
2 | 8 | 4.1622
2 | 9 | 4.0433
2 | 10 | 4.0433
2 | 11 | 4.0433
2 | 12 | 4.0433
2 | 13 | 4.1622
2 | 14 | 4.6974
2 | 15 | 5.0541
2 | 16 | 5.1731
2 | 17 | 5.2325
2 | 18 | 5.5298
2 | 19 | 5.8271
2 | 20 | 6.065
2 | 21 | 6.3623
2 | 22 | 6.6001
2 | 23 | 6.7785
2 | 24 | 6.7785
3 | 1 | 6.7913
3 | 2 | 6.6711
3 | 3 | 6.4908
3 | 4 | 6.1302
3 | 5 | 5.2888
3 | 6 | 4.6277
3 | 7 | 4.207
3 | 8 | 3.9666
3 | 9 | 3.7863
3 | 10 | 3.7863
3 | 11 | 3.8464
3 | 12 | 3.9666
3 | 13 | 4.207
3 | 14 | 4.6277
3 | 15 | 5.2888
3 | 16 | 5.7696
3 | 17 | 6.1903
3 | 18 | 6.2504
3 | 19 | 6.4307
3 | 20 | 6.611
3 | 21 | 6.8514
3 | 22 | 7.1519
3 | 23 | 7.3923
3 | 24 | 7.3923
4 | 1 | 12.4206
4 | 2 | 11.8921
4 | 3 | 11.0112
4 | 4 | 9.3375
4 | 5 | 7.5757
4 | 6 | 6.6067
4 | 7 | 6.3424
4 | 8 | 6.3424
4 | 9 | 6.4305
4 | 10 | 6.6067
4 | 11 | 6.871
4 | 12 | 7.2233
4 | 13 | 7.6638
4 | 14 | 8.2804
4 | 15 | 9.1613
4 | 16 | 9.866
4 | 17 | 10.5707
4 | 18 | 11.3635
4 | 19 | 11.8921
4 | 20 | 12.2444
4 | 21 | 12.4206
4 | 22 | 12.5087
4 | 23 | 12.4206
4 | 24 | 12.1563
5 | 1 | 11.8735
5 | 2 | 11.7063
5 | 3 | 11.0373
5 | 4 | 9.9503
5 | 5 | 9.2814
5 | 6 | 8.9469
5 | 7 | 8.7797
5 | 8 | 8.7797
5 | 9 | 8.8633
5 | 10 | 9.1142
5 | 11 | 9.4486
5 | 12 | 9.6995
5 | 13 | 9.7831
5 | 14 | 10.0339
5 | 15 | 10.5356
5 | 16 | 11.1209
5 | 17 | 11.7063
5 | 18 | 12.1243
5 | 19 | 12.2916
5 | 20 | 12.4588
5 | 21 | 12.5424
5 | 22 | 12.3752
5 | 23 | 12.2916
5 | 24 | 12.3752
6 | 1 | 14.7501
6 | 2 | 14.5083
6 | 3 | 14.0247
6 | 4 | 13.4202
6 | 5 | 12.9366
6 | 6 | 12.453
6 | 7 | 12.453
6 | 8 | 12.5739
6 | 9 | 12.9366
6 | 10 | 13.2993
6 | 11 | 13.662
6 | 12 | 14.0247
6 | 13 | 14.1456
6 | 14 | 14.7501
6 | 15 | 15.1128
6 | 16 | 15.2337
6 | 17 | 15.4755
6 | 18 | 15.7174
6 | 19 | 15.8383
6 | 20 | 15.8383
6 | 21 | 15.9592
6 | 22 | 16.0801
6 | 23 | 16.0801
6 | 24 | 15.9592
7 | 1 | 14.7542
7 | 2 | 14.6333
7 | 3 | 14.3914
7 | 4 | 13.9077
7 | 5 | 13.303
7 | 6 | 12.8192
7 | 7 | 12.5774
7 | 8 | 12.5774
7 | 9 | 12.9402
7 | 10 | 13.303
7 | 11 | 13.7867
7 | 12 | 14.2705
7 | 13 | 14.7542
7 | 14 | 15.117
7 | 15 | 15.238
7 | 16 | 14.9961
7 | 17 | 14.8752
7 | 18 | 14.7542
7 | 19 | 14.8752
7 | 20 | 14.9961
7 | 21 | 15.238
7 | 22 | 15.238
7 | 23 | 15.3589
7 | 24 | 15.238
8 | 1 | 15.9943
8 | 2 | 15.8576
8 | 3 | 15.3108
8 | 4 | 14.6272
8 | 5 | 13.6703
8 | 6 | 12.9868
8 | 7 | 12.5767
8 | 8 | 12.5767
8 | 9 | 12.9868
8 | 10 | 13.2602
8 | 11 | 13.5336
8 | 12 | 14.2171
8 | 13 | 14.6272
8 | 14 | 15.0374
8 | 15 | 15.1741
8 | 16 | 15.1741
8 | 17 | 15.1741
8 | 18 | 15.3108
8 | 19 | 15.4475
8 | 20 | 15.5842
8 | 21 | 15.8576
8 | 22 | 15.9943
8 | 23 | 15.8576
8 | 24 | 15.5842
9 | 1 | 10.4137
9 | 2 | 10.2342
9 | 3 | 9.9649
9 | 4 | 9.0671
9 | 5 | 8.1694
9 | 6 | 7.6307
9 | 7 | 7.3614
9 | 8 | 7.2717
9 | 9 | 7.2717
9 | 10 | 7.541
9 | 11 | 7.8103
9 | 12 | 8.1694
9 | 13 | 8.6183
9 | 14 | 8.9773
9 | 15 | 9.2467
9 | 16 | 9.3364
9 | 17 | 9.6955
9 | 18 | 9.9649
9 | 19 | 10.0546
9 | 20 | 10.2342
9 | 21 | 10.4137
9 | 22 | 10.5035
9 | 23 | 10.5035
9 | 24 | 10.5035
10 | 1 | 7.6863
10 | 2 | 7.4688
10 | 3 | 7.1062
10 | 4 | 6.5986
10 | 5 | 5.5835
10 | 6 | 4.5683
10 | 7 | 4.0607
10 | 8 | 3.9157
10 | 9 | 3.9882
10 | 10 | 3.9882
10 | 11 | 4.1332
10 | 12 | 4.2782
10 | 13 | 4.5683
10 | 14 | 5.3659
10 | 15 | 5.801
10 | 16 | 6.0911
10 | 17 | 6.1636
10 | 18 | 6.4536
10 | 19 | 6.8162
10 | 20 | 7.2513
10 | 21 | 7.6138
10 | 22 | 7.8314
10 | 23 | 7.9039
10 | 24 | 7.8314
11 | 1 | 6.9331
11 | 2 | 6.9985
11 | 3 | 6.9985
11 | 4 | 6.8023
11 | 5 | 6.2136
11 | 6 | 5.1017
11 | 7 | 4.4476
11 | 8 | 4.0552
11 | 9 | 3.859
11 | 10 | 3.7936
11 | 11 | 3.7936
11 | 12 | 3.7936
11 | 13 | 3.9898
11 | 14 | 4.5784
11 | 15 | 4.7747
11 | 16 | 4.8401
11 | 17 | 4.8401
11 | 18 | 4.8401
11 | 19 | 4.9709
11 | 20 | 5.2979
11 | 21 | 5.6904
11 | 22 | 6.0828
11 | 23 | 6.4752
11 | 24 | 6.7369
12 | 1 | 7.5487
12 | 2 | 7.6953
12 | 3 | 7.6953
12 | 4 | 7.5487
12 | 5 | 7.0357
12 | 6 | 5.9364
12 | 7 | 5.4233
12 | 8 | 5.0569
12 | 9 | 4.837
12 | 10 | 4.7637
12 | 11 | 4.6905
12 | 12 | 4.7637
12 | 13 | 5.0569
12 | 14 | 5.6432
12 | 15 | 5.9364
12 | 16 | 6.0096
12 | 17 | 6.0829
12 | 18 | 6.1562
12 | 19 | 6.3761
12 | 20 | 6.6692
12 | 21 | 6.9624
12 | 22 | 7.2555
12 | 23 | 7.4754
12 | 24 | 7.7686

## solar
Capital Cost Baseline | OPEX Baseline | Useful Life | Fixed OPEX Inflation Rate | Specific Yield | 1 MW Space Required | Total Energy | Fail/ year | Down-time (hrs) | Degradation per year | Existing/ Year 0 Total Cost
269000000 | 175000 | 20 | 0.1 | - | 12000 | 1769.5 | 2 | 24 | 0.8 | 80000000
per MW | per MW per month | years |  |  |  | MWh per MW per year |  | hrs | %
Months | Monthly Energy Output | Output proportion of year | average sun available hours | average sun unavailable hours |  |  | Battery Energy Storage System
1 | 151.65 | 0.085702 | 341 | 403
2 | 148 | 0.083639 | 308 | 364 |  |  | Capital Cost baseline | 110000000 | PKR per MWh
3 | 169.45 | 0.095762 | 403 | 341 |  |  | OPEX baseline fixed | 400000 | PKR per MWh per month
4 | 160.95 | 0.090958 | 390 | 330 |  |  | Useful Life | 10
5 | 157.9 | 0.089234 | 403 | 341 |  |  | Depreciation rate | 5 | %
6 | 136.65 | 0.077225 | 390 | 330 |  |  | Fixed OPEX inflation rate | 0.1
7 | 121.35 | 0.068579 | 403 | 341
8 | 128.85 | 0.072817 | 390 | 330
9 | 147.35 | 0.083272 | 403 | 341
10 | 160.7 | 0.090817 | 330 | 390
11 | 144.45 | 0.081633 | 300 | 420
12 | 143.7 | 0.081209 | 330 | 403
Month | Average Day Time (hours) | KW PV Output per MW
1 | 1 | 0
1 | 2 | 0
1 | 3 | 0
1 | 4 | 0
1 | 5 | 0
1 | 6 | 0
1 | 7 | 0
1 | 8 | 22
1 | 9 | 240
1 | 10 | 443
1 | 11 | 596
1 | 12 | 695
1 | 13 | 732
1 | 14 | 704
1 | 15 | 617
1 | 16 | 471
1 | 17 | 284
1 | 18 | 40
1 | 19 | 0
1 | 20 | 0
1 | 21 | 0
1 | 22 | 0
1 | 23 | 0
1 | 24 | 0
2 | 1 | 0
2 | 2 | 0
2 | 3 | 0
2 | 4 | 0
2 | 5 | 0
2 | 6 | 0
2 | 7 | 0
2 | 8 | 36
2 | 9 | 262
2 | 10 | 465
2 | 11 | 624
2 | 12 | 731
2 | 13 | 773
2 | 14 | 753
2 | 15 | 670
2 | 16 | 532
2 | 17 | 347
2 | 18 | 91
2 | 19 | 0
2 | 20 | 0
2 | 21 | 0
2 | 22 | 0
2 | 23 | 0
2 | 24 | 0
3 | 1 | 0
3 | 2 | 0
3 | 3 | 0
3 | 4 | 0
3 | 5 | 0
3 | 6 | 0
3 | 7 | 1
3 | 8 | 83
3 | 9 | 301
3 | 10 | 496
3 | 11 | 642
3 | 12 | 743
3 | 13 | 781
3 | 14 | 763
3 | 15 | 661
3 | 16 | 524
3 | 17 | 343
3 | 18 | 129
3 | 19 | 1
3 | 20 | 0
3 | 21 | 0
3 | 22 | 0
3 | 23 | 0
3 | 24 | 0
4 | 1 | 0
4 | 2 | 0
4 | 3 | 0
4 | 4 | 0
4 | 5 | 0
4 | 6 | 0
4 | 7 | 15
4 | 8 | 145
4 | 9 | 334
4 | 10 | 508
4 | 11 | 639
4 | 12 | 719
4 | 13 | 744
4 | 14 | 707
4 | 15 | 618
4 | 16 | 480
4 | 17 | 314
4 | 18 | 132
4 | 19 | 10
4 | 20 | 0
4 | 21 | 0
4 | 22 | 0
4 | 23 | 0
4 | 24 | 0
5 | 1 | 0
5 | 2 | 0
5 | 3 | 0
5 | 4 | 0
5 | 5 | 0
5 | 6 | 0
5 | 7 | 36
5 | 8 | 160
5 | 9 | 326
5 | 10 | 482
5 | 11 | 600
5 | 12 | 673
5 | 13 | 693
5 | 14 | 658
5 | 15 | 574
5 | 16 | 447
5 | 17 | 290
5 | 18 | 134
5 | 19 | 19
5 | 20 | 0
5 | 21 | 0
5 | 22 | 0
5 | 23 | 0
5 | 24 | 0
6 | 1 | 0
6 | 2 | 0
6 | 3 | 0
6 | 4 | 0
6 | 5 | 0
6 | 6 | 0
6 | 7 | 35
6 | 8 | 132
6 | 9 | 271
6 | 10 | 414
6 | 11 | 527
6 | 12 | 595
6 | 13 | 623
6 | 14 | 594
6 | 15 | 518
6 | 16 | 410
6 | 17 | 274
6 | 18 | 135
6 | 19 | 28
6 | 20 | 0
6 | 21 | 0
6 | 22 | 0
6 | 23 | 0
6 | 24 | 0
7 | 1 | 0
7 | 2 | 0
7 | 3 | 0
7 | 4 | 0
7 | 5 | 0
7 | 6 | 0
7 | 7 | 19
7 | 8 | 98
7 | 9 | 213
7 | 10 | 337
7 | 11 | 441
7 | 12 | 515
7 | 13 | 542
7 | 14 | 525
7 | 15 | 465
7 | 16 | 362
7 | 17 | 243
7 | 18 | 124
7 | 19 | 29
7 | 20 | 0
7 | 21 | 0
7 | 22 | 0
7 | 23 | 0
7 | 24 | 0
8 | 1 | 0
8 | 2 | 0
8 | 3 | 0
8 | 4 | 0
8 | 5 | 0
8 | 6 | 0
8 | 7 | 11
8 | 8 | 101
8 | 9 | 232
8 | 10 | 367
8 | 11 | 480
8 | 12 | 557
8 | 13 | 589
8 | 14 | 561
8 | 15 | 495
8 | 16 | 383
8 | 17 | 250
8 | 18 | 115
8 | 19 | 14
8 | 20 | 0
8 | 21 | 0
8 | 22 | 0
8 | 23 | 0
8 | 24 | 0
9 | 1 | 0
9 | 2 | 0
9 | 3 | 0
9 | 4 | 0
9 | 5 | 0
9 | 6 | 0
9 | 7 | 9
9 | 8 | 130
9 | 9 | 310
9 | 10 | 475
9 | 11 | 600
9 | 12 | 678
9 | 13 | 701
9 | 14 | 661
9 | 15 | 563
9 | 16 | 432
9 | 17 | 264
9 | 18 | 86
9 | 19 | 1
9 | 20 | 0
9 | 21 | 0
9 | 22 | 0
9 | 23 | 0
9 | 24 | 0
10 | 1 | 0
10 | 2 | 0
10 | 3 | 0
10 | 4 | 0
10 | 5 | 0
10 | 6 | 0
10 | 7 | 0
10 | 8 | 137
10 | 9 | 366
10 | 10 | 542
10 | 11 | 669
10 | 12 | 742
10 | 13 | 754
10 | 14 | 695
10 | 15 | 583
10 | 16 | 427
10 | 17 | 239
10 | 18 | 31
10 | 19 | 0
10 | 20 | 0
10 | 21 | 0
10 | 22 | 0
10 | 23 | 0
10 | 24 | 0
11 | 1 | 0
11 | 2 | 0
11 | 3 | 0
11 | 4 | 0
11 | 5 | 0
11 | 6 | 0
11 | 7 | 0
11 | 8 | 81
11 | 9 | 329
11 | 10 | 515
11 | 11 | 644
11 | 12 | 715
11 | 13 | 722
11 | 14 | 672
11 | 15 | 560
11 | 16 | 402
11 | 17 | 175
11 | 18 | 0
11 | 19 | 0
11 | 20 | 0
11 | 21 | 0
11 | 22 | 0
11 | 23 | 0
11 | 24 | 0
12 | 1 | 0
12 | 2 | 0
12 | 3 | 0
12 | 4 | 0
12 | 5 | 0
12 | 6 | 0
12 | 7 | 0
12 | 8 | 33
12 | 9 | 273
12 | 10 | 467
12 | 11 | 606
12 | 12 | 691
12 | 13 | 714
12 | 14 | 671
12 | 15 | 568
12 | 16 | 419
12 | 17 | 193
12 | 18 | 2
12 | 19 | 0
12 | 20 | 0
12 | 21 | 0
12 | 22 | 0
12 | 23 | 0
12 | 24 | 0

## grid
Capital Cost Baseline | Existing/ Year 0 Total Cost | Tariff baseline fixed | Tariff baseline variable- offpeak | Tariff baseline variable- peak | Fail/ year | Down-time (hrs) | Inflation Rate | Time to take load_primary | CO2 emissions
2000000 | 5762000 | 4077788.66 | 29390 | 37830 | 40 | 3.67 | 0.1 | 0.25 | 380
Rs. per MW for new connection | PKR | total Rs. per month | Rs. Per MWh | Rs. Per MWh | No. of Failures/Year | hours/failure |  | hr | kg/MWh

## ppa
PPA based on Solar plant source
Capital Cost Baseline | 3000000 | PKR per MW
Existing/ Year 0 Total Cost | 0 | PKR
Tariff Baseline Fixed | 7227000 | PKR per month
Tariff Baseline Variable | 30000 | PKR per MWh
Fail/ year | 2 | No.
Down-time (hrs) | 24 | hrs per downtime
Inflation Rate | 0.1
Time to take load_primary | 0.25 | hr
CO2 emissions | 0 | kg/MWh

## thermal_sources
Trifuel engine generator (HFO+RLNG) |  |  | Gas Generator |  |  | HFO Generator |  |  | Diesel Generator |  |  | Existing Gas Generators
Operating baseline | 42700 | KJ/Kg | Operating baseline | 42700 | KJ/Kg | Operating baseline | 41100 | KJ/Kg | Operating baseline | 4.714 | kWh/litre | Operating baseline | 42,700.000 | KJ/Kg | Column1
Capital Cost baseline | 153000000 | Rs./MW | Capital Cost baseline | 72000000 | Rs./MW | Capital Cost baseline | 136000000 | Rs./MW | Capital Cost baseline | 45000000 | Rs./MW | Capital Cost baseline | 72000000 | Rs./MW
OPEX baseline fixed | 300000 | Rs.MW/month | OPEX baseline fixed | 300000 | Rs.MW/month | OPEX baseline fixed | 300000 | Rs.MW/month | OPEX baseline fixed | 150000 | Rs. Per month | OPEX baseline fixed | 300000 | Rs.MW/month
OPEX baseline var | 4500 | Rs./MWh | OPEX baseline var | 3500 | Rs./MWh | OPEX baseline var | 4000 | Rs./MWh | OPEX baseline var | 1500 | Rs. Per MWh | OPEX baseline var | 3500 | Rs./MWh
Useful Life | 12 | years | Useful Life | 12 | years | Useful Life | 12 | years | Useful Life | 10 | years | Useful Life | 8 | years
Current Running Hours | 0 | hrs | Current Running Hours | 0 | hrs | Current Running Hours | 0 | hrs | Current Running Hours | - | hrs | Current Running Hours | 0 | hrs
OPEX inflation rate | 0.1 |  | Fixed OPEX inflation rate | 0.1 |  | Fixed OPEX inflation rate | 0.1 |  | Fixed OPEX inflation rate | 0.1 |  | Fixed OPEX inflation rate | 0.1
Depreciation rate | 8 | % | Depreciation rate | 8 | % | Depreciation rate | 8 | % | Depreciation rate | 8 | % | Depreciation rate | 8 | %
Cooling Load Feeding Capability | 220 | TR per MW | Cooling Load Feeding Capability | 243 | TR per MW | Cooling Load Feeding Capability | 220 | TR per MW | Cooling Load Feeding Capability | 115.5 | TR per MW | Cooling Load Feeding Capability | 243 | TR per MW
Min Loading | 30 | % | Min Loading | 30 | % | Min Loading | 30 | % | Min Loading | 30 | % | Min Loading | 30 | %
Max Loading | 98.5 | % | Max Loading | 98.5 | % | Max Loading | 98.5 | % | Max Loading | 98.5 | % | Max Loading | 98.5 | %
Failures per year | 3 |  | Failures per year | 8 |  | Failures per year | 5 |  | Failures per year | 0 |  | Failures per year | 8
Downtime per failure | 45 |  | Downtime per failure | 45 |  | Downtime per failure | 45 |  | Downtime per failure | 8 |  | Downtime per failure | 45
Time to take load_primary | 0.5 | hours | Time to take load_primary | 0.25 | hours | Time to take load_primary | 0.5 | hours | Time to take load_primary | 0.0083333 | hours | Time to take load_primary | 0.25 | hours
Time to take load_backup | 0.25 | hours | Time to take load_backup | 0.125 | hours | Time to take load_backup | 0.25 | hours | CO2 Emissions on Diesel | 800 | kg/MWh | Time to take load_backup | 0.125 | hours
CO2 Emissions on RLNG | 180 | kg/MWh | CO2 Emissions on RLNG | 180 | kg/MWh | CO2 Emissions on HFO | 270 | kg/MWh | Annual Degradation | 1 | % | CO2 Emissions on RLNG | 180 | kg/MWh
CO2 Emissions on HFO | 270 | kg/MWh | Annual Degradation | 1.5 | % | Annual Degradation | 1.5 | % |  |  |  | Annual Degradation | 1.5 | %
Gas-based operation proportion | 60 | % | Existing/ Year 0 Cost | 25000000 | PKR | [6 empty] | Capital Cost to be considered | 20000000 | PKR | to calculate depreciation
Annual Degradation | 1.5 | % | [9 empty] | Ingestion Cost | 7500000 | PKR

## site_load
Load Profile
|  |  |  | Maximum Demand Load Day | Maximum Demand Load Night | Running Load Proportion | Cooling requirement in TR | Cooling electrical load | Critical Load proportion
Site Details |  |  | Year 1 | 5 | 5 | 70 | 900 | 0.7 | 20
COP of Electric chiller | 4.5 |  | Year 2 | 5 | 5 | 70 | 900 | 0.7 | 20
cooling hours per day | 16 | hrs | Year 3 | 5 | 5 | 70 | 900 | 0.7 | 20
Critical Production load Prop | 20 | % | Year 4 | 5 | 5 | 70 | 900 | 0.7 | 20
Summer Day cooling Demand Prop | 100 | % | Year 5 | 7 | 7 | 70 | 900 | 0.7 | 20
Summer Night cooling demand Prop | 85 | % | Year 6 | 7 | 7 | 70 | 900 | 0.7 | 20
Winter Day cooling demand Prop | 85 | % | Year 7 | 7 | 7 | 70 | 900 | 0.7 | 20
Winter Night cooling demand Prop | 0 | % | Year 8 | 7 | 7 | 70 | 900 | 0.7 | 20
land area for renewables | 24281 | sqm | Year 9 | 7 | 7 | 70 | 900 | 0.7 | 20
rooftop area for solar | 24000 | sqm | Year 10 | 7 | 7 | 70 | 900 | 0.7 | 20
capital inflation rate | 0.1 | % |  | MW | MW | % | TR | MW | %
Immediate Loss from Power Failure | 4640000 | PKR
Loss as Power remains suspended | 250000 | PKR/hr
Energy Profile
|  |  | Month | Grid Peak to Non Peak Energy | Unit monthly energy consumption (MWh / MW) | Length of day (hrs) | Length of night (hrs) | Season | Days | Existing Factory
Existing Factory |  |  | 1 | 0.257 | 278.3333 | 11 | 13 | Winter | 31 | 1169
Existing Factory Maximum Demand | 4.2 | MW | 2 | 0.231 | 282.1429 | 12 | 12 | Winter | 28 | 1185
|  |  | 3 | 0.211 | 251.9048 | 13 | 11 | Summer | 31 | 1058
|  |  | 4 | 0.208 | 278.8095 | 13 | 11 | Summer | 30 | 1171
|  |  | 5 | 0.201 | 252.1429 | 13 | 11 | Summer | 31 | 1059
|  |  | 6 | 0.226 | 256.4286 | 13 | 11 | Summer | 30 | 1077
|  |  | 7 | 0.22 | 261.9048 | 13 | 11 | Summer | 31 | 1100
|  |  | 8 | 0.222 | 251.6667 | 13 | 11 | Summer | 31 | 1057
|  |  | 9 | 0.237 | 270.4762 | 12 | 12 | Summer | 30 | 1136
|  |  | 10 | 0.228 | 273.3333 | 11 | 13 | Summer | 31 | 1148
|  |  | 11 | 0.247 | 255.9524 | 10 | 14 | Winter | 30 | 1075
|  |  | 12 | 0.245 | 285.7143 | 10 | 14 | Winter | 31 | 1200

## tariff
Fuel Tariffs | Value | Units | Last Update
Natural Gas Tariff |  | Rs./MMBTU
Natural Gas Transport Cost |  | Rs./MMBTU
Natural Gas Tariff (equivalent) | 3438.89 | Rs./MWh | Updated 13th March 2023
Fuel inflation rate for Natural Gas | 0.1 |  | Updated 13th March 2023
CO2 Emissions for NG | 200 | kg/MWh
LNG Tariff |  | Rs./MMBTU
LNG Transport Cost |  | Rs./MMBTU
NG+LNG Tariff (equivalent) - 60:40 ratio | 54720.2 | Rs./MWh | Updated 13th March 2023
Fuel inflation rate for LNG | 0.1 |  | Updated 13th March 2023
CO2 Emissions for LNG | 200 | kg/MWh
LPG Tariff |  | Rs./MT
LPG Transport Cost |  | Rs./MT
LPG Tariff (equivalent) | 64000 | Rs./MWh | Updated 13th March 2023
Fuel inflation rate for LPG | 0.05
CO2 Emissions for LPG | 220 | kg/MWh
Biogas Tariff |  | Rs./MMBTU
Biogas Transport Cost |  | Rs./MMBTU
Biogas Tariff (equivalent) | 64000 | Rs./MWh
Fuel inflation rate for Biogas | 0.05
CO2 Emissions for Biogas | 0 | kg/MWh
HFO Tariff |  | Rs./MT
HFO Transport Cost |  | Rs./T
HFO Tariff (equivalent) | 38280 | Rs./MWh | Updated 13th March 2023
Fuel inflation rate for HFO | 0.05
CO2 Emissions for HFO | 400 | kg/MWh
Diesel Fuel Cost |  | Rs/Litre
Diesel Transport Cost |  | Rs/Litre
Diesel Cost Equivalent | 25180349 | Rs/MWh | Updated 13th March 2023
Fuel inflation rate for Diesel | 0.05
CO2 Emissions for Diesel | 500 | kg/MWh